## Quotation Proposal
Quotation Proposal for PV Area Civil & Installation Works (Package1,2,3,4)
I | Mian Subdivision work |  |  |  |  | Respondent's Proposal
No. | Subdiversion Works | Unit | Main Scope of Work | Settlement Rules | Settlement & Measurement Method | Package 1 (Estimated Quantity ) | Comprehensive (All-in ) Unit Rate | Quotation Subtotal | Package 2 (Estimated Quantity ) | Comprehensive (All-in ) Unit Rate | Quotation Subtotal | Package 3 (Estimated Quantity ) | Comprehensive (All-in ) Unit Rate | Quotation Subtotal | Package 4 (Estimated Quantity ) | Comprehensive (All-in ) Unit Rate | Subtotal | Quotation Subtotal
1 | Site Preparation | m² | BOQ-civil-1 Excavation & Backfilling, Foundation Treatment, Construction Site Clearing, Obstacle Removal and Waste Disposal | Settlement allowed only for fully completed work, qualified site and no residual waste. Partial work, semi-finished products and untidy site are not eligible for settlement. | Measured by actual quantity for completed & qualified single section; zero payment for unfinished section. | 1305889.66 |  |  | 1305889.66 |  |  | 1305889.66 |  |  | 1305889.66
2 | Pile Works |  | BOQ-civil-2 Foundation survey, setting out, positioning verification, drilling, embedded parts (included mounting structure), concrete pouring and testing | Settlement can be made upon completion of installation, full re-testing, complete documentation and passing quality inspection. | Measured per qualified single Nos; no payment for uninstalled or unaccepted works.
2.1 | Pile (included in mounting structure) | m | Complete mounting structure including steel piles | Refer to Item 2 | Refer to Item 2 | 122039.405 |  |  | 122039.405 |  |  | 122039.405 |  |  | 122039.405
2.2 | Type A:Pre drilling of hole (rock depth at 1.5m or or more below ground) | m | 350mm dia hole | Refer to Item 2 | Refer to Item 2 | 6716.73 |  |  | 6716.73 |  |  | 6716.73 |  |  | 6716.73
2.3 |  | m | 300mm dia hole | Refer to Item 2 | Refer to Item 2 | 38061.47 |  |  | 38061.47 |  |  | 38061.47 |  |  | 38061.47
2.4 | Type A:Pre drilling of hole (completely rock) (rock depth at just 0.4m below ground) | m | 350mm dia hole | Refer to Item 2 | Refer to Item 2 | 148.13 |  |  | 148.13 |  |  | 148.13 |  |  | 148.13
2.5 |  | m | 300mm dia hole | Refer to Item 2 | Refer to Item 2 | 839.375 |  |  | 839.375 |  |  | 839.375 |  |  | 839.375
2.6 | Type B:Ramming | m | Ramming | Refer to Item 2 | Refer to Item 2 | 12110.505 |  |  | 12110.505 |  |  | 12110.505 |  |  | 12110.505
2.7 | Type A：Plain concrete filling in the hole | m3 | 350mm dia hole to be filled with sulphate-resistant or blended concrete (Concrete Strength C25 with sulphate-resistant or blended cement) | Refer to Item 2 | Refer to Item 2 | 94.96 |  |  | 94.96 |  |  | 94.96 |  |  | 94.96
2.8 |  | m3 | 300mm dia hole to be filled with sulphate-resistant or blended concrete (Concrete Strength C25 with sulphate-resistant or blended cement) | Refer to Item 2 | Refer to Item 2 | 3163.58 |  |  | 3163.58 |  |  | 3163.58 |  |  | 3163.58
3 | Mounting Structure (tracker)& MCUs Installation |  | BOQ-E&M-1.2~1.4/1.7 Mounting columns, beams, diagonal braces, tracking system (MCUs included), connectors & accessories installation; fastening, tuning, gap adjustment, structure forming, self-check & rectification,inspection | Settlement can be made when the installation is in place, the fixation is firm, the parameters meet the standards and passed acceptance. | Measured per qualified set; no payment for uninstalled or unaccepted works.
3.1 | Mounting Structure Installation （1vx84 E-W Tracker ±60°） | set | Refer to Item 3 | Refer to Item 3 | Refer to Item 3 | 2462 |  |  | 2407 |  |  | 2377 |  |  | 2480
3.2 | Mounting Structure Installation（1vx56 E-W Tracker ±60°） | set | Refer to Item 3 | Refer to Item 3 | Refer to Item 3 | 174 |  |  | 95 |  |  | 246 |  |  | 130
3.3 | Mounting Structure Installation（1vx28 E-W Tracker ±60°） | set | Refer to Item 3 | Refer to Item 3 | Refer to Item 3 | 66 |  |  | 23 |  |  | 117 |  |  | 80
3.4 | MCUs Installation | pcs | Refer to Item 3 | Refer to Item 3 | Refer to Item 3 | 20 |  |  | 19 |  |  | 20 |  |  | 20
4 | PV Module Installation | pcs | BOQ-E&M-1.1 Module alignment, installation, clamp fastening, gap leveling, appearance protection and inspection | Settlement can be made when it's installed flat, firm, intact and qualified; no payment for loose, damaged or deviated installation. | Measured per pcs of qualified equipment/plant. | 218400 |  |  | 208152 |  |  | 216720 |  |  | 217840
5 | Cable Laying | per block | BOQ-civil-6~11 BOQ-E&M-2/4 Cable laying, connection and binding neatly; cable well construction, cable trench construction, cable backfilling, etc. | Settle after acceptance passed; no payment for unaccepted works. | Measured per qualified block. | 20 |  |  | 19 |  |  | 20 |  |  | 20
6 | Cable & Wire Installation | per block | BOQ-E&M-2/4 MV, LV & DC Cables &Wire installation, cable cabinet wiring, testing, refer to Appendix A for detail | Settle after acceptance passed; no payment for unaccepted works. | Measured per qualified block. | 20 |  |  | 19 |  |  | 20 |  |  | 20
7 | Earthing(grounding) System Installation | per block | BOQ-civil-9 BOQ-E&M-3 Construction of grounding wells, laying, welding, anti-corrosion treatment and fixing of grounding wires and main grounding system, inspection of grounding continuity, data recording | Settlement after complete laying, qualified welding, proper anti-corrosion and qualified continuity. No payment for cold solder joints, incomplete laying or missing anti-corrosion treatment. | Measured per qualified block. | 20 |  |  | 19 |  |  | 20 |  |  | 20
8 | Combiner Box Installation |  | BOQ-civil-5 BOQ-E&M-1.5~1.6 Foundation construction, support and sunshade fabrication & installation, wiring, equipment installation and testing | Settle after acceptance inspection passed; no payment for unaccepted works. | Measured per pcs of qualified equipment/plant.
8.1 | Combiner Box Installation （12+2 String Combiner Box) | pcs | Refer to Item 8 | Refer to Item 8 | Refer to Item 8 | 32.3342 |  |  | 30.7175 |  |  | 32.3342 |  |  | 32.3342
8.2 | Combiner Box Installation (14+2 String Combiner Box) | pcs | Refer to Item 8 | Refer to Item 8 | Refer to Item 8 | 547.3342 |  |  | 519.9675 |  |  | 547.3342 |  |  | 547.3342
9 | Container Inverter Installation （Inverter + MV Transformer + RMU） | pcs | BOQ-civil-4 BOQ-E&M-1.8 Foundation construction, equipment installation and testing. | Settle after acceptance passed; no payment for unaccepted works. | Measured per pcs of qualified equipment/plant. | 20 |  |  | 19 |  |  | 20 |  |  | 20
10 | Lighting and CCTV Installation |  | BOQ-civil-3/9/10/11 BOQ-E&M-5 Foundation and column（pole) construction & installation, equipment installation and testing. | Settle after acceptance passed; no payment for unaccepted works. | Measured per qualified set; no payment for uninstalled or unaccepted works.
10.1 | Lighting for Container Inverter Integrated Unit | Nos | Refer to Item 10 | Refer to Item 10 | Measured per Nos of qualified equipment/plant. | 20 |  |  | 19 |  |  | 20 |  |  | 20
10.2 | CCTV / Equipped per MV substation | Nos | Refer to Item 10 | Refer to Item 10 | Measured per Nos of qualified equipment/plant. | 20 |  |  | 19 |  |  | 20 |  |  | 20
10.3 | CCTV Local Junction Box (LJB) (Camera DB) | Nos | Refer to Item 10 | Refer to Item 10 | Measured per Nos of qualified equipment/plant. | 22.995 |  |  | 14.001 |  |  | 22 |  |  | 16.002
10.4 | Other fibers, cables and wires | per block | BOQ-E&M-5.5~5.8 Refer to Item 10 | Refer to Item 10 | Measured per qualified block. | 20 |  |  | 19 |  |  | 20 |  |  | 20
11 | SCADA Installation | set | BOQ-civil-11 BOQ-E&M-8 Foundation construction, equipment installation and testing | Settle after properly installed, firmly fixed, parameters qualified and acceptance passed. | Measured per qualified set; no payment for uninstalled or unaccepted works. | 20 |  |  | 19 |  |  | 20 |  |  | 20
12 | Weather Station Installation | set | BOQ-civil-10 BOQ-E&M-7 Foundation construction, equipment installation and testing | Settle after properly installed, firmly fixed, parameters qualified and acceptance passed. | Measured per qualified set; no payment for uninstalled or unaccepted works. | 1 |  |  | 2 |  |  | 1.519 |  |  | 1
13 | Lightning Protection |  | BOQ-E&M-6 Foundation construction, equipment installation and testing | Settle after properly installed, firmly fixed, parameters qualified and acceptance passed. | Measured per qualified set; no payment for uninstalled or unaccepted works.
13.1 | Air Terminal Fanyls for Mounting structure | set | Refer to Item 13 | Refer to Item 13 | Refer to Item 13 | 31180.2532 |  |  | 29621.2405 |  |  | 31180.2532 |  |  | 31180.2532
13.2 | Gl Lightning Arrestor for MV Stations | set | Refer to Item 13 | Refer to Item 13 | Refer to Item 13 | 20 |  |  | 19 |  |  | 20 |  |  | 20
13.3 | Lightning for MV Station Lighting pole | set | Refer to Item 13 | Refer to Item 13 | Refer to Item 13 | 20 |  |  | 19 |  |  | 20 |  |  | 20
II | Main Measurement works
No. | Items | Unit | Main Scope of Work | Settlement Rules | Settlement & Measurement Method
1 | Mobilization Fee | per block | One-time preliminary costs incurred to meet construction commencement conditions, mainly covering mobilization expenses for personnel, machinery, temporary facilities, materials, pre-construction formalities, site management, safety, environmental protection and other site entry related works. | Pile Works completed and pass the quality inspection. | Measured per block after block acceptance, no payment for unaccepted blocks, | 20 |  |  | 19 |  |  | 20 |  |  | 20
2 | Demobilization Fee | per block | When the project is completed or Party A requests the subcontractor to leave the site halfway, all the expenses related to the project's final withdrawal, transportation, demolition of temporary facilities, site clearance and restoration, coordination fees, and other compensations are included in this cost | 1.Complete site clearance, working face handover, handover of residual materials and equipment, and demolition of temporary facilities; 2.Complete for submitting construction& installation documents in case of exit the site halfway before the cold commissioning stage. | Measured per block after block acceptance, no payment for unaccepted blocks, | 20 |  |  | 19 |  |  | 20 |  |  | 20
3 | Temporary Measures Fee for construction& Installation | per block | Temporary water and electricity supply, temporary office and living facilities, temporary stacking and storage of machinery and materials, loading, unloading and transportation of equipment(plant) and materials, temporary access roads, etc. | Mounting Structure (tracker)& MCUs Installation completed and pass the quality inspection. | Measured per block after block acceptance, no payment for unaccepted blocks, | 20 |  |  | 19 |  |  | 20 |  |  | 20
4 | Safety & Civilization Fee | per block | Safety construction fee, civilized construction fee, environmental protection and soil and water conservation fee, security management fee, site management fee, daily cleaning and protection of equipment before handover | Modules, Mounting Structure (tracker), combiner boxes, Container Inverter installation completed and pass the quality inspection. | Measured per block after block acceptance, no payment for unaccepted blocks, | 20 |  |  | 19 |  |  | 20 |  |  | 20
5 | Documentation and inspection fee | per block | 1.All kinds of relating documentation fees including HSE works documents, quality inspection documents, acceptance documents, inspection application coordination. 2.All kinds of relating testing and inspection, asisting in the combine commissioning fee | 1.Settlement is available upon passing cold commissioning; 2.Provide the complete documents and got the acceptance of documents by the Party A; 3.No settlement will be conducted if cold commissioning is not completed, documents are unavailable or incomplete, or inspection application is not submitted. | Measured per block after relating documents are qualified | 20 |  |  | 19 |  |  | 20 |  |  | 20
6 | Others | per block | ALL other measurement costs which Party B consider shall incur during project implementation, Party B shall indicate and describe detail information. |  |  | 20 |  |  | 19 |  |  | 20 |  |  | 20
Total | I + II
Remarks: 1、The examples listed in "Main Scope of Work", such as "BOQ-E&M-1.2~1.4/1.7", refer to Items 1.2,1.3,1.4 and Item 1.7 in the E&M part of the BOQ. 2、This quotation list is made up only for breaks down the contract price for all works within the contract section. The subcontractor shall break down all relevant costs, profits and risk expenses arising from contract performance into each comprehensive unit price. 3、All other necessary expenses and unlisted working procedures for completing this scope of work in the Package shall be considered in the intem I[Mian Subdivision Work] and apportioned into the comprehensive unit prices.

## E&M-PV 475MW_BOQ
Main Equipment List (With Central Inverter)
S.I | Description | Type |  | Unit | Bill of Quantity | Package 1 (20 blocks) B01~B10, B18~B24 | Package 2 (19 blocks) B11~B17, B28~B39 | Package 3 (20 blocks) B40~B49, B58, B59, B66~B69, B76~B79 | Package 4 (20 blocks) B50-B57, B60-B65, B70-B75
1 | PV Plant
1.1 | PV Modules Bifacial | 720Wp Bifacial N-type Mono crystalline PV module with extended 1.2m | Part A | Pcs | 861112 | 218400 | 208152 | 216720 | 217840
1.2 | Mounting Structure | 1vx84 E-W Tracker ±60°, Corrosion resistance C4, Risk category RC2, Pre-drilled concrete piles, Terrain category II for wind (130km/h) | Part A | Set | 9516 | 2462 | 2407 | 2377 | 2480
1.3 | Mounting Structure | 1vx56 E-W Tracker ±60°, Corrosion resistance C4, Risk category RC2, Pre-drilled concrete piles, Terrain category II for wind (130km/h) | Part A | Set | 857 | 174 | 95 | 246 | 130
1.4 | Mounting Structure | 1vx28 E-W Tracker ±60°, Corrosion resistance C4, Risk category RC2, Pre-drilled concrete piles, Terrain category II for wind (130km/h) | Part A | Set | 492 | 66 | 23 | 117 | 80
1.5 | String Combiner Box | 12+2 String Combiner Box (complete in all aspect, fuses, MC4, Load Break Switch, Metalic glands, monitoring system etc.) | Part A | Pcs | 127.72 | 32.3342 | 30.7175 | 32.3342 | 32.3342
1.6 | String Combiner Box | 14+2 String Combiner Box (complete in all aspect, fuses, MC4, Load Break Switch, Metalic glands, monitoring system etc.) | Part A | Pcs | 2161.97 | 547.3342 | 519.9675 | 547.3342 | 547.3342
1.7 | MCUs | MCU (complete in all aspects) for tracker Zigbee communication, with independent lightning air-termination rod of 10mm dia and 1 meter length | Part A | Pcs | 79 | 20 | 19 | 20 | 20
1.8 | Inverter + MV Transformer + RMU | 2 X 3300 (3597KVA@40°, 20 LV input) 6600/10~35 Containerized MV Transformer station (6.6 MVA(7.19 MVA @40° , 0.66/33 kV ONAN) complete in all aspects Integrated (Inverter, transformer, LV panel, MV panel, RMU, MCCBs, ACBs, tap changer +-2.5%, all type of protections, busbars etc,) - Integrated communication box for Combiner boxes data collection + ODF for Trafo Communication - Metalich Glands for cable entries with earthing mechanisim - MV Cable termination boots for double runs for single phase | Part A | Pcs | 79 | 20 | 19 | 20 | 20
2 | MV, LV & DC Cables
2.1 | Power cable (String) | 1.8kV 1C x 6mm2 CU/XLPO/XLPO/Tin coated (Red) | Part A | m | 1794880 | 454400 | 431680 | 454400 | 454400
2.2 | Power cable (String) | 1.8kV 1C x 6mm2 CU/XLPO/XLPO/Tin coated (Black) | Part A | m | 1794880 | 454400 | 431680 | 454400 | 454400
2.3 | String Cable Connector | Set Male/Female - (2 pairs per string) (pack of 1000 pcs) | Part A | m | 64 | 16 | 16 | 16 | 16
2.4 | LVDC Cables (From CB to Central Inverter) (UV Resistant) | 240mm2 - Single - Core - AL/XLPE/PVC/AWA/PVC (Voltage Level: 1.9kV/3.3kV) (Red) | Part A | Part A | 0 | 0 | 0 | 0 | 0
2.5 | LVDC Cables (From CB to Central Inverter) (UV Resistant) | 240mm2 - Single - Core - AL/XLPE/PVC/AWA/PVC (Voltage Level: 1.9kV/3.3kV) (Black) | Part A | Part A | 0 | 0 | 0 | 0 | 0
2.6 | LVDC Cables (From CB to Central Inverter) (UV Resistant) (@30C ground temperature and 1 cable at fuse rating 400A) | 300mm2 - Single - Core - AL/XLPE/PVC/AWA/PVC (Voltage Level: 1.9kV/3.3kV) (Red) | Part A | Part A | 0 | 0 | 0 | 0 | 0
2.7 | LVDC Cables (From CB to Central Inverter) (UV Resistant) (@30C ground temperature and 1 cable at fuse rating 400A) | 300mm2 - Single - Core - AL/XLPE/PVC/AWA/PVC (Voltage Level: 1.9kV/3.3kV) (Black) | Part A | Part A | 0 | 0 | 0 | 0 | 0
2.8 | LVDC Cables (From CB to Central Inverter) (UV Resistant) (@30C ground temperature and 1 cable at fuse rating 400A) | 400mm2 - Single - Core - AL/XLPE/PVC/AWA/PVC (Voltage Level: 1.9kV/3.3kV) (Red) | Part A | m | 78500 | 19873.4177 | 18879.7468 | 19873.4177 | 19873.4177
2.9 | LVDC Cables (From CB to Central Inverter) (UV Resistant) (@30C ground temperature and 1 cable at fuse rating 400A) | 400mm2 - Single - Core - AL/XLPE/PVC/AWA/PVC (Voltage Level: 1.9kV/3.3kV) (Black) | Part A | m | 78500 | 19873.4177 | 18879.7468 | 19873.4177 | 19873.4177
2.10 | LVDC Cables (From CB to Central Inverter) (UV Resistant) (@30C ground temperature and 1 cable at fuse rating 400A) | 500mm2 - Single - Core - AL/XLPE/PVC/AWA/PVC (Voltage Level: 1.9kV/3.3kV) (Red) | Part A | m | 300000 | 75949.3671 | 72151.8987 | 75949.3671 | 75949.3671
2.11 | LVDC Cables (From CB to Central Inverter) (UV Resistant)(@30C ground temperature and 1 cable at fuse rating 400A) | 500mm2 - Single - Core - AL/XLPE/PVC/AWA/PVC (Voltage Level: 1.9kV/3.3kV) (Black) | Part A | m | 300000 | 75949.3671 | 72151.8987 | 75949.3671 | 75949.3671
2.12 | Combiner box LVDC Cable Lug | Two End Terminal Set for AL/XLPE/AWA/PVC 1C-240mm2 | Part A | No. | 0 | 0 | 0 | 0 | 0
2.13 | Combiner box LVDC Cable Lug | Two End Terminal Set for AL/XLPE/AWA/PVC 1C-300mm2 | Part A | No. | 0 | 0 | 0 | 0 | 0
2.14 | Combiner box LVDC Cable Lug | Two End Terminal Set for AL/XLPE/AWA/PVC 1C-400mm2 | Part A | No. | 512 | 1541.7722 | 1464.6835 | 1541.7722 | 1541.7722
2.15 | Combiner box LVDC Cable Lug | Two End Terminal Set for AL/XLPE/AWA/PVC 1C-500mm2 | Part A | No. | 8648 | 308.3544 | 292.9367 | 308.3544 | 308.3544
2.16 | Power cable (For MCUs & WS, Light poles) | 3C (2C+ G) 2.5mm2 - CU/XLPE/PVC (Voltage Level: 0.6/1kV) | Part A | m | 8200 | 2075.9494 | 1972.1519 | 2075.9494 | 2075.9494
2.17 | Cable termination tubes | Heat Shrink tubes, for 300sqmm x 8 inch | Part A | m | 0 | 0 | 0 | 0 | 0
2.18 | Cable termination tubes | Heat Shrink tubes, for 400sqmm x 8 inch | Part A | m | 563.2 | 1695.9494 | 1611.1519 | 1695.9494 | 1695.9494
2.19 | Cable termination tubes | Heat Shrink tubes, 500sqmm x 8 inch | Part A | m | 5188.4375 | 1313.5285 | 1247.8521 | 1313.5285 | 1313.5285
2.20 | MV Cable | 240 mm² 1C Al\XLPE/CWS/PVC/AWA/PVC 19/33kV cable(s) between MV stations, Fire resistant, Low smoke low halogen cables | Part A | m | 96650 | 28060 | 26298 | 29645 | 27997
2.21 | MV Cable | 400 mm² 1C Al\XLPE/CWS/PVC/AWA/PVC 19/33kV cable(s) between MV stations, Fire resistant, Low smoke low halogen cables (@7600KVA at 30C temp) | Part A | m | 229950 | 11361.96 | 10392.216 | 12942.66 | 11303.04
2.22 | MV Cable | 630 mm² 1C Al\XLPE/CWS/PVC/AWA/PVC 19/33kV cable(s) from MV stations to 33kV SWGR Fire resistant, Low smoke low halogen cables (@7600KVA at 30C temp) | Part A | m
2.23 | Indoor MV Cable Termination | 185 mm² 1C AL/XLPE cable terminations on 33 kV GIS switchgear (C-type seperable screened connectors,Heat shrinkable, complete incl. earth kits and surge arrester) | Part A | set of 3 |  | 0 | 0 | 0 | 0
2.24 | Indoor MV Cable Termination | 240 mm² 1C AL/XLPE cable terminations on 33 kV GIS switchgear (C-type seperable screened connectors,Heat shrinkable, complete incl. earth kits and surge arrester) | Part A | set of 3 | 120 | 22.0253 | 20.9241 | 22.0253 | 22.0253
2.25 | Indoor MV Cable Termination | 400 mm² 1C AL/XLPE cable terminations on 33 kV GIS switchgear (C-type seperable screened connectors,Heat shrinkable, complete incl. earth kits and surge arrester) | Part A | set of 3 | 40 | 12.6582 | 12.0253 | 12.6582 | 12.6582
2.26 | Cable Joint 1Cx185sqmm | Heat Shrink jointing kit resin encapsulated type, for 19/33kV 1Cx185sqmm, Outdoor type, Rated Impulse withstand level>=200kV, with earth kit | Part A | set of 3 |  | 0 | 0 | 0 | 0
2.27 | Cable Joint 1Cx240sqmm | Heat Shrink jointing kit resin encapsulated type, for 19/33kV 1Cx240sqmm, Outdoor type, Rated Impulse withstand level>=200kV, with earth kit | Part A | set of 3 | 53 | 13.4177 | 12.7468 | 13.4177 | 13.4177
2.28 | Cable Joint 1Cx630sqmm | Heat Shrink jointing kit resin encapsulated type, for 19/33kV 1Cx400sqmm, Outdoor type, Rated Impulse withstand level>=200kV, with earth kit | Part A | set of 3 | 260 | 65.8228 | 62.5316 | 65.8228 | 65.8228
2.29 | Link box with sheath voltage limiter (SVL) | For MV(19/33) cable grounding, 2kV SVL | Part A | set | 5 | 2 | 1 | 1 | 1
2.30 | Link box | Earthing link box without SVL for MV (19/33) cable termination | Part A | set | 5 | 2 | 1 | 1 | 1
2.31 | String Cable Conduit | HDPE Cable conduit DN50 with sealant and elbows (assumed 80 meter length per combiner box) | Part B | m | 183175.2 | 46373.4684 | 44054.7949 | 46373.4684 | 46373.4684
2.32 | PVC, DN50 for Road Crossing (DC String Cable) | DN50 UPVC for Ductbank of DC String Cable Road Crossing | Part B | m | 2290 | 579.6684 | 550.6849 | 579.6684 | 579.6684
3 | Earthing
3.1 | GI Round Earthing wire Dia 12mm | For earthing mesh PV Area | Part B | m | 197500 | 50000 | 47500 | 50000 | 50000
3.2 | GI Round Earthing wire 70mm2 | For earthing mesh (MV Station) (80 meters per MV station) | Part B | m | 6320 | 1600 | 1520 | 1600 | 1600
3.3 | Bare Copper Earthing wire 35mm2 | Earthing Conductor for MV Station lighntning Arrestor | Part B | m | 1580 | 400 | 380 | 400 | 400
3.4 | Copper Rod Ø16mm, 2m each | For earthing mesh (PV+MV Station) | Part B | Pcs | 566 | 143.2911 | 136.1266 | 143.2911 | 143.2911
3.5 | BVR - 1 x 25 mm2 | For combiner box/inverter grounding | Part B | m | 2518.659 | 637.6352 | 605.7534 | 637.6352 | 637.6352
3.6 | BVR - 1 x 6 mm2 (UV Resistant Copper Cable) + nut and bolts | For PV Panel grounding | Part B | m | 172300 | 43620.2532 | 41439.2405 | 43620.2532 | 43620.2532
3.7 | 35 mm2 x M10 tin-coated compression lugs | For tracker earthing termination (2-pcs per tracker) | Part B | m | 23903 | 6051.3924 | 5748.8228 | 6051.3924 | 6051.3924
3.8 | Bare Copper Earthing wire 70mm2 + Lugs + nut and bolts | For MV cable trench earthing | Part B | m | 66275 | 13526.58 | 19057.984 | 25133.955 | 8548.4
3.9 | Earthing BVR Earthing cable (Weather Station + MV Station Light, MCU) | 35mm2 Yellow Green PVC Insulated | Part B | m | 1105 | 273 | 273 | 279.7468 | 273
3.10 | Bimetallic compression lugs for earthing conductor (for CBs) | 35mm 2* M10 | Part B | No. | 4716.7614 | 1194.1168 | 1134.411 | 1194.1168 | 1194.1168
3.11 | Earthing BVR Earthing cable for LVDC Cable armouring earthing | 16mm2 tin-coated braided cable (1-.5 meter per cable termination) | Part B | m | #REF! | 4856.5823 | 4613.7532 | 4856.5823 | 4856.5823
3.12 | LVDC Cable armouring earthing compression lugs | 16mm2* M8 tin-coated 0-type compression lugs (4 pcs per combiner box considering 2 cable runs per CB) | Part B | Pcs | 2602.824 | 629.3387 | 343.7918 | 955.7387 | 674.0051
3.13 | Exothermic earthing cable joints for PV area earthing mesh | 35 mm2 T- joints, cross-joints, straight joints | Part B | Nos | 15919.69 | 4029.6684 | 3797.6849 | 4073.6684 | 4017.6684
4 | Miscellaneous
4.1 | Cable Ties UV resistant | Cable Ties For string cables of PVC (8 inch each) (single tie at each 0.5 meter distance) (pack of (100) | Party A | Nos | 24124.023 | 6117.342 | 5829.243 | 6071.52 | 6101.55
4.2 | Steel cable ties for HDPE conduits fixing with structure pile for down string cables | 0.5m x 5mm size (16 ties per CB/Inverter) | Party B | Nos | 18317.52 | 4637.3468 | 4405.4795 | 4637.3468 | 4637.3468
4.3 | Fire retardant foam for LVDC, String and MV cable | 1 Botle of 0.5 litter per Combiner Box | Party B | Ltr | 1144.845 | 289.8342 | 275.3425 | 289.8342 | 289.8342
4.4 | Fire Proof mud putty | 10kg per MV Station | Party B | kg | 790 | 200 | 190 | 200 | 200
5 | Lighting and CCTV
5.1 | Inverter Station lighting | 90W LED Light + Mounting pole 5m | Part A | Nos | 79 | 20 | 19 | 20 | 20
5.2 | CCTV Fixed Type Bullet Camera per MV station with bracket (with Intrusion Detection System) | 5megapixels, OUTDOOR FIXED BODY, IP CAMERA Effective Range 50mtrs | Part A | Nos | 79 | 20 | 19 | 20 | 20
5.4 | CCTV Local Junction Box (LJB) (Camera DB) | IP67 Box (including Surge Arrestor+Video Switch (E/F)+2 x FOPP+Earthing Cable) | Part A | Nos | 75 | 22.995 | 14.001 | 22 | 16.002
5.5 | Fiber Optic | 12C SM Fiber Optic Cable | Part A | m | 110000 | 37617.9544 | 16894.8 | 30910.9517 | 24575.8305
5.7 | Ethernet Cat 6 wire | Cat6 Ethernet Cable (POE) for CCTV from CCTV DB to camera | Part A | m | 331.8 | 84 | 79.8 | 84 | 84
5.8 | 0.6/1kV, CU/XLPE/SWA/PVC, Fire-retardant | 2C-4mm² | Part A | m | 20750 | 5271.873 | 4565.268 | 6848.64 | 4064.64
6 | PV Area lightening Protection
| Air Terminal Fanyls for Mounting structure | lnclude 1x Air Termination Rod 1.8m(Horizontal) + 0.9m ( Vertical l0mm Diameter, 2x Folding Clamp sets of M10 hex screws, flat washers, hex nuts, (Galv steel or aluminum) | Part A | Set | 123162 | 31180.2532 | 29621.2405 | 31180.2532 | 31180.2532
| Gl Lightning Arrestor for MV Stations | Include 6m lightning mast with finial of 1m, with 3 concrete foundation base, pole diameter to be 60mm. Aluminium | Part A | Set | 79 | 20 | 19 | 20 | 20
| Lightning for MV Station Lighting pole | Insulated Lightning Protection Kit with insulated 70sqmm cable, including the clamp and accessories. Installation on (5.1) MV Station lighting pole. | Part A | Set | 79 | 20 | 19 | 20 | 20
7 | Weather Station
| Weather Station and independend Sensor | Meteorological station (complete in all aspect). Global horizontal irradiance:1x digital pyranometers (Class A, IEC61724, ISO9060) Global Inclined Irradiance: 1x digital pyranometers (Class A, IEC61724, ISO9060), to measure the incident irradiation on the plane of the modules; • Albedometer (at the primary weather station only): 1x digital thermopile pyranometers (Class A, IEC61724, ISO9060); • 1 x Ambient temperature sensor (shielded ventilated); • 1 x Air humidity sensor (shielded ventilated); • 2 x Module temperature sensors as minimum (final quantity according to IEC 61724-1); • 1 x Air pressure sensor; • 1 x Wind speed sensor; • 1 x Wind direction sensor; • 1 x Rain level sensor; • 1 x Soiling ratio measuring station, according to IEC 61724 and including both measurement methods 1 and 2; and, • Lightning detection/warning system (at the primary weather station and if required by the LRA only). • Independend lightning arrestor • Mouting Structure towers • Battery + PV panel with mounting racks etc. | Part A | Set | 6 | 1 | 2 | 1.519 | 1
8 | PV Area Field SCADA
| PV Field SCADA Panels | • PV Ethernet Switch • UPS with battery (8Hrs Backup) • 1 no. SCADA Controller • 2 nos. Fiber Optic Patch Tray • AC&DC Circuit Breakers Sheet Steel 2.5mm, IP Class: IP66 | Part A | SET | 79 | 20 | 19 | 20 | 20
| Communication Box Field structure (For PV field scada panels and Coverter DB's) | Front and Back Hood (including Channel iron , lip channel, Base plates) Materual : 1.6MM Mild Steel Plate CNC Cut And Bent Finish : Hot Dip Galvanized | Part A | SET | 79 | 20 | 19 | 20 | 20
| Coverter DB's for combiner box communication | IP Class: IP66 Complete in all aspects including • Fiber/ RS485 converter (2 Pcs per Converter DB) • FOPP (2 Pcs per Converter DB) with patch cords and pigtails • Two pole circuir breakers • Power Supply unit • SPD • Fuse etc. | Part A | SET | 79 | 20 | 19 | 20 | 20
| Fiber Optic Cable | 4C SM Fiber Optic Cable for combiner box communication with converter DB | Part A | m | 144654 | 35274.0258 | 35370 | 37320 | 36690
| Control cable 0.6/1kV, CU/XLPE/SWA/PVC, Fire-retardant | 2C-2.5mm² ,From MV Station LV panel to PSSU and CCTV DB | Part A | m | 1896 | 480 | 456 | 480 | 480
| Ethernet Cat 6 Cable | Cat6 Ethernet Cable - for PV SCADA to MET Station - for PV SCADA to SCU - for PV SCADA to Tracker Controller Box -for Converter DB's to PSSU panels(PV SCADA) | Part A | m | 4508.4 | 1104 | 1124.4 | 1176 | 1104

## Civil-PV 475MW_BOQ
ACED NOTSI PV SOLAR PROJECT SOUTH AFRICA 475MW
Civil Works
NOTES: M30 and M15 concrete refers to concrete having 28 days cylinder strength of 30MPa and 15MPa respectively.
The segreggation quantities are approximiate may change as per latest detailed design.
SI | Description | Remark | Unit | Package 1 (20 blocks) B01~B10, B18~B24 | Package 2 (19 blocks) B11~B17, B28~B39 | Package 3 (20 blocks) B40~B49, B58, B59, B66~B69, B76~B79 | Package 4 (20 blocks) B50-B57, B60-B65, B70-B75
A-1.00 | PV Plant
| Clearing and grubbing | Cleared from vegetation. | m2 | 1305889.66 | 1305889.66 | 1305889.66 | 1305889.66
| Topsoil removal | soil stripping 0.15m | m3 | 0 | 0 | 0 | 0
| Filling (imported material) | Each filled area to be compacted to at least 85%MDD at OMC, I) Insitu preparation of above mentioned filling area II) The imported material shall comply with standard material grade G7 or G8 as a minimum. | m3
| Filling (material recovered from cutting) | Filled area to be compacted to at least 85%MDD at OMC, I) Insitu preparation of above mentioned filling area II) The approved material recovered from cutting to grade shall be used for filling. III) Fill material shall be free from all sort organic content e.g. plant roots etc. | m3 | 34788.431 | 15793.5389 | 2236.1225 | 2195.3387
| General Cutting (to achieve grade) | Soft Material Excavation | m3 | 18392.1293 | 6411.6318 | 4891.8339 | 5692.2147
| General Cutting (to achieve grade) | Rock Excavation | m3 | 7882.3411 | 2747.8422 | 2096.5002 | 2439.5206
2 | Piles | No. of piles updated as per Archtech information 3 strings 13 piles 2 strings 9piles 1 string 5 piles (current qtys are based on latest General layout with 1,2 & 3 string configurations_REV-1. (1Px28 : 286nos. , 1Px56 : 645nos. ,1Px84 : 9726) 80% of the piles are concrete encased piles (Type A), and 20% are ramming (Type B)）. | Nos | 33902 | 32261 | 33700 | 33810
| Pile (included in mounting structure) | Complete mounting structure including steel piles | m | 122039.405 | 122039.405 | 122039.405 | 122039.405
| Type A:Pre drilling of hole (rock depth at 1.5m or or more below ground) | 350mm dia hole | m | 6716.73 | 6716.73 | 6716.73 | 6716.73
|  | 300mm dia hole | m | 38061.47 | 38061.47 | 38061.47 | 38061.47
| Type A:Pre drilling of hole (completely rock) (rock depth at just 0.4m below ground) | 350mm dia hole | m | 148.13 | 148.13 | 148.13 | 148.13
|  | 300mm dia hole | m | 839.375 | 839.375 | 839.375 | 839.375
| Type B:Ramming | Ramming | m | 12110.505 | 12110.505 | 12110.505 | 12110.505
| Type A：Plain concrete filling in the hole | 350mm dia hole to be filled with sulphate-resistant or blended concrete (Concrete Strength C25 with sulphate-resistant or blended cement) | m3 | 94.96 | 94.96 | 94.96 | 94.96
|  | 300mm dia hole to be filled with sulphate-resistant or blended concrete (Concrete Strength C25 with sulphate-resistant or blended cement) | m3 | 3163.58 | 3163.58 | 3163.58 | 3163.58
3 | Lightning mast Structure and foundation | Foundation for ESE 6.0 Meter Lightning Rod with Terminal Base | Set | 40 | 38 | 40 | 40
| Excavation (rock) |  | m3 | 96.1 | 91.295 | 96.1 | 96.1
| Backfill |  | m3 | 49.535 | 47.0583 | 49.535 | 49.535
| M15 lean concrete |  | m3 | 4.805 | 4.5648 | 4.805 | 4.805
| M30 Concrete |  | m3 | 41.76 | 39.672 | 41.76 | 41.76
| Reinforcement |  | ton | 3.132 | 2.9754 | 3.132 | 3.132
| Structural Steel |  | ton | 0.96 | 0.912 | 0.96 | 0.96
4 | MV(Inverter) Station foundation and UPS Foundation | Isolated type foundations for the portaCabin/Container type buildings (Supported at 8 points) | NO. | 20 | 19 | 20 | 20
| Excavation (rock) |  | m³ | 547.224 | 519.8628 | 547.224 | 547.224
| Backfill |  | m³ | 404 | 383.8 | 404 | 404
| M15 lean concrete |  | m³ | 23.04 | 21.888 | 23.04 | 23.04
| M30 Concrete |  | m³ | 104.96 | 99.712 | 104.96 | 104.96
| Reinforcement |  | Tons | 5.248 | 4.9856 | 5.248 | 5.248
| Steel stair |  | Tons | 9.6 | 9.12 | 9.6 | 9.6
| Embedded Plates |  | Tons | 4 | 3.8 | 4 | 4
5 | Combiner Box Suppport, shield & Foundations |  |  | 579 | 551 | 580 | 580
| Excavation (rock) |  | m³ | 86.85 | 82.65 | 87 | 87
| lean concrete |  | m³ | 4.632 | 4.408 | 4.64 | 4.64
| Concrete |  | m³ | 92.64 | 88.16 | 92.8 | 92.8
| Reinforcement |  | tons | 4.632 | 4.408 | 4.64 | 4.64
| Structural Steel |  | tons | 23.4604 | 22.3258 | 23.5009 | 23.5009
A-6 | Trench A | DC STRING CABLES
| Excavation | Soft Material Excavation | m3 | 5106.75 | 4845.75 | 5139.75 | 4845.75
| Excavation | Rock excavation | m3 | 1702.25 | 1615.25 | 1713.25 | 1615.25
| Backfill soil |  | m3 | 6809 | 6461 | 6853 | 6461
| Warning Tape |  | m | 34917 | 33133 | 35142 | 33133
A-7 | Trench B | LVDC Power Cables
| Excavation | Soft Material Excavation | m3 | 23682.75 | 22488.75 | 23740.5 | 22488.75
| Excavation | Rock excavation | m3 | 7894.25 | 7496.25 | 7913.5 | 7496.25
| Backfill soil |  | m3 | 23683 | 22489 | 23741 | 22489
| Sand Filling |  | m3 | 7894 | 7496 | 7913 | 7496
| Warning Tape |  | m | 131570 | 124938 | 131891 | 1214938
| Cable marker |  | pcs | 1032 | 977 | 1052 | 977
A-8 | Trench C | MV Cables Trenches
| Excavation | Soft Material Excavation | m3 | 14652.75 | 10460.25 | 9083.25 | 9838.5
| Excavation | Rock excavation | m3 | 4884.25 | 3486.75 | 3027.75 | 3279.5
| Sand Filling |  | m3 | 5582 | 3985 | 3460 | 3748
| Backfill soil |  | m3 | 13955 | 9962 | 8651 | 9370
| Warning Tape |  | m | 62022 | 44275 | 38447 | 41646
| Cable marker |  | m | 448 | 379 | 317 | 334
A-9 | Trench D | PV + MV STATIONS+ EARTHING
| Excavation | Soft Material Excavation | m3 | 10592.25 | 10026 | 11426.25 | 10111.5
| Excavation | Rock excavation | m3 | 3530.75 | 3342 | 3808.75 | 3370.5
| Backfill soil |  | m3 | 14123 | 13368 | 15235 | 13482
A-10 | Trench E | MCU +WEATHER STATIONS+MV STATION LIGHTNING ARRESTOR+ MV STATION LIGHTING & CCTV+FENCE CCTV
| Excavation | Soft Material Excavation | m3 | 661.5 | 660 | 683.25 | 683.25
| Excavation | Rock excavation | m3 | 220.5 | 220 | 227.75 | 227.75
| Sand Filling |  | m3 | 313 | 313 | 323 | 323
| Backfill soil |  | m3 | 569 | 567 | 588 | 588
A-11 | Trench F | PV Field SCADA Looping, Fence CCTV & Combiner Box Communication
| Excavation | Soft Material Excavation | m3 | 8052.75 | 6524.25 | 7775.25 | 7109.25
| Excavation | Rock excavation | m3 | 2684.25 | 2174.75 | 2591.75 | 2369.75
| Sand Filling |  | m3 | 4956 | 4015 | 4785 | 4375
| Backfill soil |  | m3 | 5781 | 4684 | 5582 | 5104
Note on C29: 批注: 批注: 李海阳: is it including the inverters?