南非475MW诺希光伏电站项目

Notsi 475MW PV PROJECT in South Africa

# 集中控制楼及保安室建筑工程技术规范书

Technical Specification of O&M Building Civil Work and Guard Room

目录Content

集中控制楼及保安室建筑工程技术规范书	1

1 工程概况General Overview	1

2 现场条件Site Conditions	1

3 缩写与定义Abbreviations and Definitions	3

4 工程承包范围 Scope of Work	4

5 工作界面与接口 Working Interface	10

6 技术要求 Technical Requirements	12

7 现场管理Site Management	56

8 附件Attachment	69

工程概况General Overview

工程名称 Project Name

南非475MW诺希光伏电站项目

Notsi 475MW PV PROJECT in South Africa

工程地点Project Location

项目位于南非自由州省Dealesville西南约15公里处。该项目可通过S322公路在Dealesville处的次级公路R64抵达。

The project is located approximately 15 kilometers southwest of Dealesville, Free State Province, South Africa. It can be accessed via the R64 secondary road from Dealesville, connected to the S322 highway

工程规模Project Description

新建一座交流容量为475MW（直流620MW）光伏发电站，本项目包括一栋集中控制楼和一个保安室。

Construct a new photovoltaic power station with an AC installed capacity of 475 MW (DC capacity: 620 MW).This project includes a O&M building and a Guard house.

现场条件Site Conditions

自然条件Natural Conditions

    - 气候条件Climate Conditions

| Parameter | Unit | Value |
| --- | --- | --- |
| Maximum ambient temperature in the shade, to be taken as air inlet temperature for air-conditioning and ventilation | °C | 25 |
| Average annual ambient temperature | °C | 15.5 |
| Minimum ambient temperature | °C | -2 |
| Minimum design ultimate wind speed | m/s | 40 |
| Maximum relative humidity | % | 93 |
| Average annual relative humidity | % | 37 |
| Minimum relative humidity | % | 34 |
| Maximum Annual rainfall | mm | 620 |
| Maximum elevation above sea level | m.a.s.l. | 1236.6 |

    - 地形、地勘及水文条件Topography, Geological Exploration And Hydrological Conditions

  - 详细情况见附件1-地形报告， 附件2-地勘报告，附件3-水文报告 。

  - Please refer to Annex 1-3 for topographic, geotechnical and hydrological report.

施工条件Construction Conditions

    - 施工水源Water Supply

现场无施工水源，乙方需根据现场实际情况设置必要的临时储水设施和用水措施，不允许钻探取用地下水。乙方需采取有效措施合理规划用水，避免水资源的浪费。

No supply water on site. The Party B needs to set up necessary temporary water storage facilities and water supply measures according to the actual situation on site. Drilling for groundwater is not allowed. The Party B needs to take effective plan to save supply water and avoid waste.

    - 排水Drainage

现场无市政排污接入点，乙方需根据现场实际情况设置临时化粪池和排污设施，严禁现场直排生活污水和施工废水，排污设施需满足南非当地的环保要求。

The Party B must set up temporary septic tanks and sewage facilities according to the actual situation on site as no municipal sewage connect point on site. It is strictly prohibited to directly discharge domestic sewage and construction wastewater in site. The sewage facilities must meet the local environmental protection requirements of South Africa.

    - 施工电源Power Supply

现场无直接电源，乙方需根据现场实际情况设置临时柴油发电机供电。

No power supply on site, and the Party B needs to set up a temporary diesel generator to supply power according to the actual situation on site.

    - 施工便道Construction Access

乙方需对施工便道进行清理、压实，以满足交通和设备通行的需求。

The Party B need clean and compact the construction access for acceptability of traffic and equipment access.

    - 临建设施Temporary Facilities

甲方提供场地，乙方的临建设施由乙方自行考虑。临建设施需要满足乙方和业主的现场安全管理标准和临建场地规划，临建设施在工程完工后7天内清理并恢复原始地貌或按甲方要求执行。

Party A provides the site, and Party B's temporary facilities are considered by Party B. Temporary facilities need to meet the site safety management standards and temporary site planning of Party B and the owner. Temporary facilities shall be cleaned up and restored to the original landform within 7 days after the completion of the project or as required by Party A.

缩写与定义Abbreviations and Definitions

| Abbreviations | Description |
| --- | --- |
| KSA | The Kingdom of South Africa |
| AC | Alternating Current |
| DC | Direct Current |
| FF | Firefighting and Fire Alarm |
| PACU | Packaged Air Conditioning Unit |
| HVAC | Heating Ventilation and Air Conditioning |
| HCIS | High Commission for Industrial Security |
| SBC | South Africa Building Code |
| IBC | International Building Code |
| ISO | International Organization for Standardization |
| OHTL | Overhead Transmission Lines |
| SEC | South Africa Electricity Company |
| BOQ | Bill of Quantity |
| MCC | Mechanical Completion Certificate |
| ICOD | Initial Commercial Operation Date |
| PCOD | Provisional Commercial Operation Date |
| Party A | Tender(甲方) |
| Party B | Party B(乙方) |

工程承包范围 Scope of Work

总则General

本工程分为集控中心建筑工程，门卫室建筑工程，工作内容包括但不限于：施工准备与进场、材料采购与仓储、施工许可、施工道路修建、现场清理、土方工程、基础工程、土方回填及压实、主体结构、砌筑、抹灰与油漆、地面、吊顶、屋面、门窗、给排水、照明、暖通空调、建筑防雷与接地、室外通道、电缆桥架安装、电缆铺设、电气设备安装、预留孔洞及封堵、屋面安装，安全管理，质量管理，资料收集与归档，缺陷清单闭合等，具体见建筑及结构专业图纸。

This project is divided into the construction of the O&M building and the construction of the guard house. The work content includes but not limited to: construction preparation and entry, material procurement and storage, construction permit, construction road construction, site clearance, earthwork, foundation work, earthwork backfilling and compaction, main structure, masonry, plastering and painting, flooring, ceiling, roof, doors and windows, water supply and drainage, lighting, HVAC (heating, ventilation, and air conditioning), building lightning protection and grounding, outdoor passageway, cable tray installation, Cable Installation, electrical equipment installation, reserved holes and sealing, roof installation, safety management, quality management, data collection and archiving, closure of defect list, etc. Please refer to the architectural and structural professional drawings for details..

施工准备及动员Preparation and Mobilization

施工准备及动员包括但不限于：审查图纸、熟悉项目相关资料、编制施工方案、技术交底、建立测量控制网、现场临建布置、制定采购计划、材料采购准备、施工机械准备、人员培训、管理人员及施工人员进场、技术培训等。

Construction preparation and mobilization includes but not limited to: checking drawings,  familiar with project-related information,preparing construction method statement,technical disclosure of method statement,establishing survey control network,site temporary lay down area, specifying procurement plans,material procurement preparations,construction machinery preparations,personnel training,entry of management personnel and construction personnel, technical training, etc.

材料采购及仓储Material Supply and Storage

材料采购及仓储包括但不限于：材料报审、材料采购、材料进场验收、仓库建设、预制场地及组装场地规划与建设、材料管理、材料二次转运、甲供材料卸货及保管等。

Material procurement and storage includes but not limited to: material submission, material procurement, on-site material acceptance, warehouse construction, plan and built the prefabrication area and assembly area, material management, secondary transportation, unloading and storage of Party A's materials, etc.

施工许可Work Permit

施工许可包括但不限于：根据业主和南非当地政府的要求，配合甲方提供办理施工许可的相关资料；约定由乙方负责的施工许可由乙方办理并提交甲方备案。

Construction permits include but not limited to: cooperating with Party A to provide relevant information for obtaining construction permits according to the requirements of the owner and the local South Africa government; the construction permits agreed to be the responsibility of Party B shall be processed by Party B and submitted to Party A for record .

加工图的绘制与提交Shop Drawing Submission

乙方根据甲方提供的基础设计图纸绘制用于实际指导施工的详细加工图，包括但不限于，基础结构尺寸、上部结构尺寸、钢筋料表、模板支撑体系、地面地砖布局、钢结构制件等其他甲方或业主要求绘制的图纸，并附带相关计算书和其他说明提交甲方审核。

Party B shall draw detailed shop drawings for actual construction guidance based on the basic design drawings provided by Party A, including but not limited to foundation structure dimensions, superstructure dimensions, steel bar cut schedule, shuttering system, floor tile layout, steel structure components and other drawings required by Party A or the owner, and submit it to Party A for review attach with relevant calculation sheets and other instructions.

施工便道Construction Access

乙方负责标段范围内现场所有施工所需的便道包括但不限于：现场车辆通行的道路、重型机械通行或作业的道路、施工通道、人员通道和平台、必要的标识和警示标志、必要的照明设施、道路的日常维护与保养等。

Party B is responsible for all access required for on-site construction within the scope of the bidding section, including but not limited to: roads for on-site vehicle traffic, roads for heavy machinery traffic or operation, construction passages,walkway and platform,necessary identification and warning signs, necessary lighting facilities, daily maintenance and upkeep of roads, etc.

场地清理Site Cleaning

乙方应清理施工范围内所有的植被、灌木丛、垃圾、大型石块、金属物、移除树根、特殊或指定植物的保护（保护标志和围栏）与特殊或限定植物的移植（移植方案需获得批准）。清理的垃圾及杂物需按照南非本地安全管理规定和环境保护规定进行回收处理，其他符合南非本地法律的环境保护要求等。

Party B shall clear all vegetation, shrubs, garbage, large stones, metals, tree roots, protection measures for special or designated plants (including protection signs and fences), and transplantation of special or restricted plants (the transplantation plan must be approved). The cleared garbage and debris shall be recycled and disposed of in accordance with local safety management regulations and environmental protection regulations in South Africa, as well as other environmental protection requirements in line with local laws in South Africa.

土方工程Earthwork

土方工程包括但不限于：土方开挖、基底压实、承载力试验、回填土选用及运输、土方回填及压实、边坡防护、边坡支护、弃土转运等。

Earthwork includes but not limited to: excavation, base compaction, bearing capacity test, backfill soil selection and transportation, backfilling and compaction, slope protection, slope support, and waste soil transportation.

集中控制楼O&M Control Building

包括但不限于：土方工程、混凝土垫层、钢筋、各类预埋（管）件制作及安装、预埋套管制作及安装、模板工程、混凝土浇筑及养护、基础混凝土防水、框架结构、砌体工程、抹灰及涂料工程、地面工程、吊顶工程、屋面工程、门窗工程、给排水工程、照明工程、暖通工程、建筑防雷及接地、电气设备安装、室外散水、预留孔洞及封堵、钢结构补漆等全部与集控楼相关的施工工作。

  - Including but not limited to: earthwork, concrete bedding layer, steel bars, fabrication and installation of various pre-installed (pipes) components, fabrication and installation of pre-installed sleeves, formwork engineering, concrete pouring and curing, waterproofing of foundation concrete, frame structure, masonry engineering, plastering and coating engineering, flooring engineering, ceiling engineering, roof engineering, door and window engineering, water supply and drainage engineering, lighting engineering, HVAC engineering, building lightning protection and grounding, electrical equipment installation，outdoor drainage, reserved holes and sealing, steel structure paint repair, ect All construction works related to the O&M Control Building.

门卫室 Guard House

包括但不限于：土方工程、混凝土垫层、预埋（管）件、预埋套管、基础工程、砌体工程、抹灰及涂料工程、地面工程、吊顶工程、屋面工程、门窗工程、给排水工程、照明工程、暖通工程、建筑防雷及接地、室外散水、预留孔洞及封堵等。

  - Including but not limited to: earthwork, concrete bedding, pre-installed (pipes), pre-installed sleeves, foundation works, masonry works, plastering and coating works, flooring works, ceiling works, roofing works, door and window works, water supply and drainage works, lighting works, HVAC works, building lightning protection and grounding, outdoor drainage, reserved holes and sealing, etc.

建筑防雷及接地Building Lightning Protection and Earthing

建筑防雷及接地包括但不限于：建筑结构接地、建筑屋面接地、避雷引下线、室内接地干线、建（构）筑物等电位联结、防雷接闪器安装。施工所需的材料、焊接工具等均由乙供。

Building lightning protection and grounding includes but is not limited to: building structural grounding, building roof grounding, lightning down conductors, indoor grounding main line, equipotential bonding of buildings (structures), installation of lightning protection lightning arresters. The materials and welding tools required for construction are all provided by Party B.

照明Normal Lighting

照明包括但不限于：照明线管及线槽安装、照明线管防腐、吊杆安装、电缆敷设、接线盒安装、照明灯具安装、应急灯具安装、照明控制面板安装及接线、开关插座安装、防水防爆开关安装、测试及调试等。

Lighting includes but is not limited to: installation of lighting conduits and troughs, anti-corrosion treatment of lighting conduits, installation of suspension rods, cable laying, installation of junction boxes, installation of lighting fixtures, installation of emergency lighting, installation of lighting control panels and wiring, installation of switches and sockets, installation of waterproof and explosion-proof switches, testing and debugging, etc.

暖通工程HVAC

工作内容包括包括但不限于：室外空调机组安装、风管吊杆及支架安装、风管及阀门安装、风机安装、控制电缆敷设及端接、开关箱安装、控制面板安装、设备接地、试验及调试等。

The work content includes but not limited to: Installation of outdoor air conditioning units, installation of duct hangers and supports, installation of ducts and valves, installation of fans, laying and termination of control cables, installation of switch boxes, installation of control panels, grounding of equipment, testing and commissioning, etc.

给排水工程Plumbing System

给排水工程包括但不限于：室内外给水管道及配件安装、室内外排水管道及配件安装、阀门安装、雨水管道及配件安装、管道与化粪池及污水池的连接、给水设备安装、稳压泵安装、水箱安装、洗手台安装、卫生洁具安装、试验及调试等。

Water supply and drainage engineering includes but is not limited to: installation of indoor and outdoor water supply pipelines and accessories, installation of indoor and outdoor drainage pipelines and accessories, installation of valves, installation of rainwater pipes and accessories, connection of pipes to septic tanks and sewage tanks, installation of water supply equipment, installation of pressure stabilizing pumps, installation of water tanks, installation of washbasins, installation of sanitary fixtures, testing and commissioning, etc.

屋面工程Roof

包括但不限于：檩条安装、彩钢板制作与安装、雨水檐口制作与安装。

Including but not limited to: installation of roof beams, fabrication and installation of color steel plates, and fabrication and installation of rainwater eaves.

电气设备安装工程Electrical equipment installation

包括但不限于：电话和网络、电缆、盘柜、监控、消防系统、门禁的安装。

Including but not limited to: O&M building telephone and LAN network, cable , panel ,CCTV System,  Fire Detection and Alarm System,access control system Installation.

HSE安全管理HSE management

### 详见附件HSE安全管理

Refer to Annex8 :HSE Management Agreement of Construction and Installation Works for PV Area

.

质量管理QA/QC management

详见附件质量管理

Refer to Annex9 :Penalty Provision for Non-compliance with the Project Management.

资料收集与归档Documents

资料收集与归档包括但不限于：开工报告、施工方案、施工组织设计、施工计划、质量验收计划（表）等技术文件的编制与报审；施工过程记录（电缆敷设记录和试验记录等）、验收资料、技术文件、竣工图的收集、整理、编制、归档、移交等。

Documents collection and archiving include but not limited to: preparation and submission of technical documents such as commencement report, method statement,work schedule, organization chart, inspection test plan; collection, sorting, preparation, archiving, and transfer of construction  records (cable laying records and test records, etc.), inspection documents, technical documents, and drawings.

尾项消缺TOP Punch list

按照甲方及业主要求，对TOP尾项、调试期间尾项进行消除并提交关闭单。

According to the requirements of Party A and the owner, Party B has to obtain necessary approval on TOP walkdown’s. The closeout is to be submitted for final handing over and for necessary authorized approval.

工作界面与接口 Working Interface

总则General

本标段以建筑散水外0.5m内作为工作范围的界限。

This section takes the area 0.5 m outside the building's stormwater drainage as the boundary of the working scope.

与永久道路接口Permanent road interface

以永久道路的边界为接口。

The interface is the boundary of the permanent road.

电气接口

照明接口：乙方负责建筑室内照明。

Lighting interface: Party B is responsible for the building's indoor lighting.

照明箱接口：照明箱至灯具的管路及线缆由乙方负责；照明配电箱由其他分包负责。

Lighting distribution box interface: Party B is responsible for the pipes and cables from lighting to lamps; other subcontractors are responsible for the lighting distribution box.

防雷接地接口：建筑结构接地、建筑屋面接地由乙方负责完成。

Lightning protection grounding interface: The grounding of the building structure and the building roof shall be completed by the contractor.

电缆保护管：墙体地面的套管安装、开孔及最终的修复由乙方负责。

Cable protection pipe: The installation of the sleeves on the walls and floors, the drilling of holes, and the final repair shall be the responsibility of the contractor.

给排水接口：就地控制箱、事故按钮的安装、电缆敷设及端接由其他分包负责，剩余工作由乙方负责。

Water supply and drainage interface: The installation of the local control box and emergency button, cable laying and termination shall be the responsibility of other subcontractors, and the remaining work shall be the responsibility of Party B.

消防接口Fire fighting interface

消防套管与墙（地）面孔洞封堵由乙方负责，消防管与套管之间的封堵由乙方负责。

The sealing of the holes in the walls (or floors) for fire protection pipes and the pipes themselves shall be the responsibility of the contractor.

其他Others

土建工作正式完成前的安全防护措施、垃圾清理及积水清理等由乙方负责。

Party B shall be responsible for safety protection measures, garbage removal and waterlogging removal before the formal completion of the civil engineering work.

技术要求 Technical Requirements

总则General

- 本工程的技术要求要满足业主主合同、设计资料、厂家资料、图纸及规范标准的相关技术要求及规定，并且需满足业主及项目部的验收要求。本工程执行过程中，如有关规定存在分歧，应以最高标准要求为准，所用标准和技术规范均为最新版本。具体应满足南非建筑法规，包括但不限于以下现行技术规程、规范和标准（以现行有效版本为准）。

The technical requirements of this project must comply with the relevant technical requirements and regulations stipulated in the owner's main contract, design documents, manufacturer's data, drawings and standards. It must also meet the acceptance requirements of the owner and the project department. During the execution of this project, if there are any differences in relevant regulations, the highest standard requirements shall prevail. The standards and technical specifications used are all the latest versions. Specifically, it should meet the South African building regulations, including but not limited to the following current technical procedures, norms and standards (based on the current valid version).

| 序号SN | 名 称Name | 编号NO. |
| --- | --- | --- |
| 1 | General Principles | SANS 10400-A |
| 2 | Structural Requirements | SANS 10400-B |
| 3 | Site & Environmental Safety | SANS 10400-D |
| 4 | Plumbing | SANS 10400-P |
| 5 | Roof & Roof Drainage | SANS 10400-L |
| 6 | Fire Protection | SANS 10400-T |
| 7 | Concrete structures | SANS 10100:2019 |
| 8 | Portland cement | SANS 50197 |
| 9 | Concrete test methods | SANS 3001 |
| 10 | Masonry construction | SANS 10164 |
| 11 | Civil Engineering Standard Specification | SANS 1200 |
| 12 | Water supply & drainage installation | SANS 10252 |
| 13 | Electrical installation code | SANS 10142:2021 |

- 若上述文件均无明确要求，至少满足如下要求：

If none of the above documents are clearly required, at least the following requirements:

场地清理Site Cleaning

- 乙方应清理施工范围内所有的植被、灌木丛、垃圾、大型石块、金属物、废弃桩基、淤泥、沟槽内的石膏或类似材料、移除树根、地表以下0.5米内的树桩和根须、有机土层，特殊或指定植物的保护（保护标志和围栏）与特殊或限定植物的移植（移植方案需获得批准）。清理的垃圾及杂物需按照南非本地安全管理规定和环境保护规定进行回收处理，其他符合南非本地法律的环境保护要求等。

Party B should to removal of all vegetation, brush, rubbish, large stones, metal material, abandoned pile foundation, silt, occurring within the limit of construction, gypsum or similar material in trench, root removal, stumps and roots to a depth of 0.5 meters below the ground, organic soil, protection of special or designated vegetation (protection signs and fences), transplantation of special or designated vegetation (transplantation method need to be approved), cleaned garbage shall be recycled in accordance with South Africa HSE management regulations, others that meet the local law environmental protection requirements of KSA, etc.

- 废弃物由乙方负责处理，处理方式需符合南非本地本地法律的环境保护要求。

Party B shall be responsible for the disposal of waste, and the disposal method must comply with the environmental protection requirements of local South Africa laws.

土方工程 Earthwork

    - 土方开挖excavation

- 在施工前, 乙方应详细了解工程地质结构、地形地貌和水文地质情况。

Before execution the Party B shall have a detailed understanding of the geological structure, topography and hydrogeology of the project.

- 土方开挖前应按照甲方的动土安全规章编制安全施工措施，向HSE部申请办理动土作业许可。挖掘机必须由专业人员操作，操作人员应通过相关专门培训机构的专门培训，并持证上岗。

Before excavation, safety construction measures shall be prepared in accordance with the Safe Work Procedure by Party A, and the permit for excavation shall be applied to the HSE Department. The excavator must be operated by professionals, and the operators should pass the special training of the relevant specialized training institutions, and hold a certificate to work.

- 土方开挖的顺序应根据图纸及现场情况制定，基础土方开挖采用人工开挖和机械开挖相结合的方法。开挖至基底设计标高以上300mm时，采用人工开挖至设计标高，避免扰动地基，严禁超挖。

The sequence of excavation should be determined according to the drawings and on-site conditions. The foundation excavation adopts a combination of manual excavation and mechanical excavation. When excavation reaches 300mm above the design elevation of the base, manual excavation is used to the design elevation to avoid disturbing the foundation. Over-excavation is strictly prohibited.

- 在开挖过程中产生的土方，所有适合回填的材料应重复使用，无法使用的土方需弃置在指定位置。

All excavated material if suitable for backfilling should be reused, and unusable material should be shifted at a designated location.

- 当开挖深度超过1米时，需要考虑自然放坡，临近建筑物或其他无法满足放坡要求时应该充分支护防止土方坍塌；当土方开挖深度超过3米时，乙方须采取分层放坡或边坡加固措施，并编制专项施工方案报甲方审批。

When the excavation depth is more than 1 m, it is necessary to consider the natural slope, and the adjacent structures or other conditions that cannot meet the slope requirements should be fully supported to prevent the soil collapse; When the excavation depth exceeds 3 meter, Party B shall take measures of layering or reinforcing the slope, and prepare a special method statement and submit it to Party A for approval.

- 基坑开挖应有足够的宽度，每边至少预留1米空间，确保具有足够的工作空间。

The foundation pit excavation should be wide enough, with at least 1 meter of space reserved on each side to ensure sufficient working space.

- 毗邻现有公用设施的开挖须以人工开挖。

Excavation adjacent to existing utility facilities shall be excavated manually.

- 采取洒水、覆盖等措施减少开挖过程中的扬尘污染。

Take measures such as watering and covering to reduce dust pollution during excavation.

- 土方不应堆在基坑边缘，以防坍塌。

Excavated Soil should not be piled at the edge of the pit to prevent collapse.

- 基坑周围应设置合适的硬防护。

Appropriate barriers should be set up around the foundation pit.

- 夜间施工时，应有足够的照明设施；在危险地段应设置明显标志。

When construction is carried out at night, there should be sufficient lighting facilities and obvious signs should be set up in dangerous areas.

- 开挖完成后，地基的承载力应满足设计及相关规范要求。

After the excavation is completed, the bearing capacity of the foundation base shall meet the design and relevant specifications.

- 用于场区回填的土，从现场开挖取土，取土点距离集控中心距离小于3.2公里。（如有）

The soil used for backfilling shall be excavated on site, and the distance between the soil excavation point and O&M building shall be less than 3.2 km.（if have）

    - 回填backfilling

- 土方回填前，基础面质量的应符合甲方验收标准。

Before backfilling, the quality of the foundation surface should comply with Party A's acceptance standards.

- 土方回填前应清理底部，确认垃圾、杂物、石块和尖锐碎片等已经清理干净。

Before backfilling, clean the bottom and make sure that garbage, foreign matter, rocks and sharp debris have been removed.

- 回填材料应分层堆放并压实，直至达到要求的标高。施工时每一层都应倾斜排水。压实前的每层厚不得超过250mm。如果不能使用移动机械设备，则应使用打夯机或平板夯将材料彻底压实。

Backfill material shall be placed and built-up in successive layers and compacted, until it has reached the required elevation. Each layer shall be sloped to drain during construction. Layers shall not be allowed to exceed 250mm in thickness before compaction. Where mobile mechanical equipment cannot be used, the materials shall be thoroughly compacted by the use of tamping rammer or plate compactor.

- 平整区域应平滑、压实、无不规则的表面变化，并倾斜排水。与设备和建筑物相邻的最终面应低于完成的地面标高，为保持适当的排水应从地基边放坡。在任何进一步施工之前，处于道路、地基或其他受力区域下的所有平整区域都应有一个夯实的地基，该地基至少包括顶部15公分粗平并参照改良的普氏击实试验（ASTM D- 1557) 压实至最大密度的 95%。所有路堤、非支撑和未铺砌区域上15公分的回填应参照改良的普氏击实试验（ASTM D- 1557) 至少压实至最大密度的90%，除了沟填土和道路下方的填土应参照改良的普氏击实试验（ASTM D- 1557) 压实至最大密度的 95%。

Graded areas shall be smooth, compacted, free from irregular surface changes, and sloped to drain. Final earth grade adjacent to equipment and buildings shall be below finished floor elevations and shall be sloped away from foundations as necessary to maintain proper drainage. Prior to any further construction all graded areas under roadways, foundations, or other supportive areas shall have a compacted subgrade consisting of at least the top 15 cm scarified and compacted to 95% of the maximum density based on the modified proctor test (ASTM D-1557) density. Backfill for all embankments, non-supportive and unpaved areas shall be compacted to at least 90% of the maximum density based on the modified proctor test (ASTM D-1557) in 15 cm lifts, except trench fill and fill beneath roads shall be compacted to 95% of the maximum density based on the modified proctor test (ASTM D-1557).

- 取土开挖的基坑，应回填并回复原地貌。（如有）

The excavated foundation pit should be backfilled and restored to its original shape. (If have)

垫层Lean concrete

- 垫层混凝土的强度等级C20，28天强度应达到20Mpa。

The strength grade of the lean concrete is C20, and the strength after 28 days should reach 20Mpa.

- 混凝土垫层浇筑前，需将基层表面应清理干净并铺设满足设计要求的聚乙烯薄膜。

Before pouring the concrete cushion layer, the surface of the base layer should be cleaned and covered with a polyethylene film that meets the design requirements.

- 混凝土垫层浇筑中，需要注意保持其浇筑的连贯性，避免出现冷缝或施工缝。且应采用平板振动器进行振捣，确保混凝土的均匀性和密实性。

When pouring the concrete, it is necessary to maintain the continuity of the pouring to avoid cold joints or construction joints. Needle vibrator should be used for vibration to ensure the uniformity and density of the concrete.

- 控制浇筑速度与高度，确保混凝土能够均匀、稳定地铺设在基层上。

Control the pouring speed and height to ensure that the concrete can be laid evenly and stably on the base.

- 对于较厚的垫层，可采用分层浇筑法。分层浇筑时，应确保每层混凝土的厚度均匀，且振捣分层进行。

For thicker layers, pouring can be used and different sections. When pouring in layers, ensure that the thickness of each layer of concrete is uniform and vibrate each layer properly and use bonding agent.

- 混凝土垫层浇筑完成后应及时进行养护，保持混凝土表面湿润，防止水分蒸发过快导致干裂。

After the concrete is poured, it should be curing in time to keep the concrete surface moist to prevent the water from evaporating too quickly and causing cracking.

基础防水卷材Waterproof membrane of foundation

- 防水卷材施工前将基层表面的灰尘、油污等杂物彻底清除干净，确保基层表面干净整洁同时基层应平整。

Before waterproofing membrane construction, thoroughly remove dust, oil and other debris on the surface of the base layer to ensure that the surface of the base layer is clean and tidy and the base layer should be flat.

- 均匀涂刷胶粘剂，确保胶层无沉淀、无凝块、无离析现象。

Apply adhesive evenly to ensure that there is no precipitation, clots or segregation in the adhesive layer.

- 卷材之间的搭接宽度不得小于100mm，上下两层和相邻两幅卷材接缝应错开三分之一幅度，确保接缝处的防水性能。

The overlap width between the membranes shall not be less than 100 mm, and the joints between the upper and lower layers and the adjacent two membranes shall be staggered by one-third to ensure the waterproof performance of the joints.

- 边铺贴边排除卷材下面的空气和多余的胶粘剂，保证卷材与基层面以及各层卷材之间粘结密实，无空鼓、无脱落现象。

Remove the air and excess adhesive under the membrane while laying it to ensure that the membrane and the base layer and between each layer of membrane are tightly bonded, without hollowing or falling off.

- 使用专用的固定工具或特有的固定方式将卷材固定在基层上，避免其在使用中发生脱落。

Use special fixing tools or special fixing methods to fix the membrane on the base layer to prevent it from falling off during use.

- 对卷材的搭接处进行密封处理，使用防水胶将接缝处进行涂抹，并确保涂层均匀、完整。

Seal the overlap of the membrane, apply waterproof glue to the joints, and ensure that the coating is uniform and complete.

- 垂直面的防水卷材，使用满足要求的保护板；水平方向的防水卷材浇筑满足要求的混凝土保护层。

For vertical waterproofing membranes, use protective plates that meet the requirements; for horizontal waterproofing membranes, cast a concrete protective layer that meets the requirements.

- 防水卷材压条选择应满足设计及规范要求，压条与卷材之间的缝隙处填充密封材料，确保密封严密无遗漏，且涂抹均匀，厚度适中，避免过多或过少导致密封效果不佳。

The selection of waterproof membrane layer strips should meet the design and specification requirements. The gap between the layer strips and the membrane should be filled with sealing materials to ensure that the seal is tight and there are no omissions. The material should be applied evenly and the thickness should be moderate to avoid excessive or insufficient application that may lead to poor sealing effect.

模板工程 Formwork

- 乙方应负责模板和支架的材料供应、设计、制作、运输、安装和拆除等全部模板作业。模板的设计、制作和安装应保证模板结构有足够的强度和刚度，能承受混凝土浇筑和振捣的侧向压力和振动力，防止产生移位，确保混凝土结构外形尺寸准确，并应有足够的密封性，以避免漏浆。

The Party B shall be responsible for all formwork operations such as material supply, design, production, transportation, installation and dismantling of formwork and brackets. The design, fabrication and installation of the formwork shall ensure that the formwork structure has sufficient strength and rigidity to withstand the lateral pressure and vibration force of concrete pouring and pounding, to prevent displacement, to ensure the accurate shape and size of the concrete structure, and to have sufficient sealing to avoid slurry leakage.

- 模板的制作应满足施工图纸要求的建筑物结构外形，其制作允许偏差不应超过南非国家有关规程规范的规定。

The fabrication of the formwork should meet the requirements of the construction drawings for the structural shape of the building, and the allowable deviation of its production should not exceed the provisions of the relevant South Africa national regulations and specifications.

- 除施工图纸或甲方另有规定外，模板的材料、制作、安装及拆除均应按南非政府规定执行。

The material, fabrication, installation and removal of formwork shall be in accordance with South Africa government regulations unless otherwise specified on the construction drawings or by the Party A.

- 模板表面涂刷界面剂，便于模板拆除，模板的拆除应符合设计要求，还应遵守南非国家标准或行业相关规范的规定。

Apply interface agent on the surface of the formwork to facilitate its removal. The removal of the formwork should meet the design requirements and comply with the provisions of South Africa national standards or relevant industry specifications.

钢筋工程reinforcement

- 乙方应负责钢筋材料的采购、运输、验收和保管，并应对钢筋进行进场材质检验和验点入库，乙方应通知甲方参加检验和验点工作；检验和验点时，乙方应向甲方提交钢筋原材料的质量证明文件，并在甲方的见证下进行钢筋取样送检和复试。

The Party B shall be responsible for the purchase, transportation, acceptance and storage of reinforcing steel materials, and shall inspect the incoming material and check the points of steel into the warehouse, and the Party B shall notify the Party A to participate in the inspection and check the points; when inspecting and checking the points, the Party B shall submit to the Party A the quality certification documents of the raw material of reinforcing steel, and shall take samples of reinforcing steel for inspection and retesting under the witness of the Party A.

- 钢筋应为符合设计图纸的规定。钢筋制作与绑扎应符合南非的规范。

The reinforcing bars must comply with the specifications outlined in the design drawings. The fabrication and binding of the reinforcing bars should adhere to the standards of South Africa.

- 钢筋加工的尺寸应符合设计图纸的要求。

The size of the steel bar after processing should meet the requirements of the design drawings.

- 钢筋安装顺序与位置与图纸相符。

The sequence and position of steel bar installation shall be consistent within the drawings.

- 绑扎时应保证钢筋的横平竖直，接头位置应符合规范要求，且绑扎牢固，无松动变形现象。

When binding, the steel bars should be kept horizontal and vertical, the joint positions should meet the requirements of the specifications, and the binding should be firm without looseness or deformation.

- 钢筋保护层的垫块应采用定型混凝土垫块，厚度误差不超过5mm。

The pads for the steel bar cover should be shaped concrete pads with a thickness error not exceeding 5 mm.

- 乙方负责所有预埋（管）件和预埋套管的加工、制作、安装；应按施工图纸所示的位置预埋各种埋件，埋件安装误差不能大于图纸和设备厂家要求的精度。

The Party B is responsible for the fabrication and installation of all embedded （pipe） plate and embedded sleeve pipe; All kinds of embedded parts should be embedded according to the location of the construction drawings, and the installation error of embedded parts should not be more than the precision required by the drawings and equipment manufacturers.

混凝土工程concrete

    - 混凝土浇筑Concrete pouring

- 本工程所有混凝土均需采用商品混凝土，商品混凝土供应商的资质应符合南非政府的相关规定。

All concrete for this project shall be commercial concrete, and the qualification of the commercial concrete supplier shall be in accordance with the relevant regulations of the South Africa  government.

- 必须严格按照设计要求进行混凝土的配合比设计，确保混凝土强度、工作性和耐久性满足工程需求。

The concrete mix design must be carried out strictly in accordance with the design requirements to ensure that the concrete strength, work ability and durability meet the project needs.

- 水泥、水、砂、石子等原材料应符合南非相关标准，并经过检验合格后方可使用。

Raw materials such as cement, water, sand, and gravel must comply with relevant South Africa standards and can only be used after passing inspection.

- 在混凝土浇筑过程中，乙方应按有关规定和甲方的指示，在混凝土运输车出料口和浇筑现场进行混凝土取样试验.

During the concrete pouring process, the Party B shall, in accordance with relevant regulations and the instructions of the Party A, conduct concrete sampling tests at the concrete transport vehicle outlet and at the pouring site.

- 在施工前四周，乙方应提供详细的浇筑说明。在高温条件下工作应仔细研究，在高温条件下工作应仔细研究，混凝土的运输、放置、压实和处理将按照本地和国际标准和良好的工业惯例进行。

Four weeks prior to construction, the Party B shall present the detailed pouring instructions of the foundation, solutions for problems posed by large volumes, thick elements, requirements for tight tolerances, hard to reach areas and the very dense areas of reinforcement. Work in conditions of high heat should be carefully studied, The concrete will be transported, placed, compacted and its treatment will be made in accordance with Local and international standards and following good industrial practice. The more stringent standards will be chosen as a reference.

- 混凝土浇筑前检查模板及支撑系统的刚度、稳定性和密封性，确保无变形、无漏浆；支撑系统应牢固可靠，能承受混凝土浇筑时的侧压力和施工荷载。

Before pouring concrete, check the rigidity, stability and sealing of the formwork support system to ensure there is no deformation or leakage; the support system should be firm and reliable and able to withstand the lateral pressure and construction load during concrete pouring.

- 预埋管、预埋套管等预埋件应提前安装好，位置准确，固定可靠。

Embedded parts such as embedded pipes and embedded sleeve pipes should be installed in advance, with accurate positioning and reliable fixation.

- 混凝土浇筑前准备好混凝土运输车、泵车、振捣器等浇筑设备与工具，并检查其性能是否良好。

Before pouring concrete, prepare concrete transport trucks, pump trucks, vibrators and other pouring equipment and tools, and check whether their performance is good.

- 任何部位混凝土开始浇筑前8h（隐蔽工程为12h），乙方必须通知甲方对浇筑部位的准备工作进行检查，检查内容包括但不仅限于：地基处理、已浇筑混凝土面的清理以及模板、钢筋、插筋、预埋件等的埋设和安装等，经甲方检查验收合格后，方可进行混凝土浇筑。

8h (12h for concealed works) before the concrete is poured in any part, the Party B must inform the Party A to check the preparation work of the poured part, including but not limited to: foundation treatment, cleaning of the poured concrete surface and the burial and installation of formwork, reinforcement, inserts, pre-buried parts, etc. Only after the Party A's inspection and acceptance can the concrete be poured.

- 任何部位混凝土开始浇筑前，乙方应将该部位的混凝土浇筑申请单提交甲方审核，经甲方批准后，方可进行混凝土浇筑。

Before concrete pouring starts in any part, the Party B shall submit the application form for concrete pouring in that part to the Party A for review and approval.

- 混凝土应在初凝前浇筑完毕，避免产生冷缝；当层间间歇时间超过混凝土初凝时间时，应按施工缝处理。

Concrete pouring should be completed before initial setting to avoid cold joints; when the interval time between layers exceeds the initial setting time of concrete, it should be treated as a construction joint.

- 混凝土自由下落高度不宜超过2m，超过时应采用串筒、溜槽等工具辅助下料；在竖向结构中限制自由倾落高度不宜超过3m，以防混凝土离析。

The free fall height of concrete should not exceed 2m. If it exceeds this height, tools such as string tubes and chutes should be used to assist in unloading. In vertical structures, the free fall height should not exceed 3m to prevent concrete segregation.

- 混凝土应分层浇筑，每层浇筑厚度满足相关规定。

Concrete should be poured in layers, and the thickness of each layer should meet relevant regulations.

- 振捣时间要使混凝土表面出现浆液，无气泡、无下沉。

The vibration time should be sufficient to allow slurry to appear on the concrete surface without bubbles or sinking.

- 因技术或设备限制不能连续浇筑时，应留置施工缝，施工位置需满足相关标准及甲方同意。

When continuous pouring is not possible due to technical or equipment limitations, construction joints should be left, and the construction location must meet relevant standards and be agreed by Party A.

- 浇筑完成后应及时进行养护，保持混凝土表面湿润，防止水分蒸发过快导致干裂，持续时间不得少于14天。

After pouring, maintenance should be carried out in time to keep the concrete surface moist to prevent rapid evaporation of water and cracking. The duration should not be less than 14 days.

    - 混凝土表面处理Concrete surface treatment

混凝土表面处理包括：混凝土表面缺陷处理、设置倒角及涂刷防水油漆等，具体要求按相关图纸要求执行。

The surface treatment of concrete includes: handling of concrete surface defects, setting chamfers, and applying waterproof paint, etc. The specific requirements shall be carried out in accordance with the relevant drawings.

- 混凝土表面必须洁净，无浮灰、水泥渣及疏松部位。

The concrete surface must be clean, free of floating dust, cement residue and loose parts.

- 若混凝土表面粗糙，应选择合适的涂料、修补材料进行修复。

If the concrete surface is rough, appropriate coatings and repair materials should be selected for repair.

- 在所有混凝土工程正式验收之前，乙方均要加以维护和保护。浇筑块的棱角和突出部分更应加强保护。

All concrete work is to be maintained and protected by the Party B until formal acceptance of the work. The corners and protruding parts of the cast blocks should be even more protected.

- 要求涂刷防水涂料的混凝土外露部分涂刷满足设计要求的防水涂料，涂刷完成后表面无褶皱、鼓包、空鼓。

The exposed parts of the concrete that require waterproof coating should be coated with the waterproof material that meets the design requirements. After the coating is applied, there should be no wrinkles, bulges or hollowing on the surface.

砌体工程Block wall

- 用于本工程的砌块品种、规格、标号均应满足设计要求；乙方在确定供货厂家前，应向甲方递交样品，并提请甲方批准；在进场验收时，应向甲方提供符合南非国家现行质量标准的出厂合格证，否则，甲方有权拒绝验收或使用，由此造成的相关经济损失由乙方承担。

The types, specifications and grades of block wall used in this project shall meet the design requirements. Before determining the supplier, the Party B shall submit samples to the Party A and seek approval from the Party A. During on-site acceptance, the Party B shall provide the Party A with a factory certificate that complies with the current South Africa national quality standards. Otherwise, the Party A has the right to refuse acceptance or use, and the relevant economic losses caused thereby shall be borne by the Party B.

- 乙方应向甲方提交砌筑砂浆配合比设计和强度试验报告，以保证砌筑砂浆的强度满足设计要求；砌筑砂浆配合比和强度试验报告报经甲方审查批准后，方可使用。

The Party B shall submit the masonry mortar mix design and strength test report to the Party A to ensure that the strength of the masonry mortar meets the design requirements; the masonry mortar mix design and strength test report may only be used after being reviewed and approved by the Party A.

- 砌筑前砖应提前洒水湿润，砌筑过程中严禁用水冲浆灌缝；上下层错缝，内外搭砌，避免出现连续的垂直通缝。

Bricks should be sprinkled with water to moisten them before laying, and it is strictly forbidden to use water to flush mortar and fill joints during the laying process; the upper and lower layers should be staggered, and the inside and outside should be laid to avoid continuous vertical joints.

- 各种预留洞、埋件、拉结筋按设计要求留置，避免后剔凿，影响砌体质量。

Various reserved holes, embedded parts and tie bars should be retained according to design requirements to avoid subsequent chiseling and affecting the quality of the masonry.

- 灰缝宽度、砂浆饱满度应满足南非标准或行业规范的规定。

The width of the mortar joints and the fullness of the mortar should meet the requirements of South Africa standards or industry specifications.

- 对需要灌浆的空心砖墙体进行检查，确认墙体无倾斜且根基稳固。

Check the hollow brick wall that needs grouting to confirm that the wall is not tilted and the foundation is stable.

- 对墙体上存在的缝隙进行填充修复，以确保注浆效果。

Fill and repair the gaps on the wall to ensure the grouting effect.

- 灌浆过程中注意观察浆液的流向和饱满度，确保灌浆均匀且充分。

During the grouting process, pay attention to the flow direction and fullness of the slurry to ensure that the grouting is uniform and sufficient.

- 如发现灌浆不足或有空缺区域，应及时补充灌浆材料，确保墙体内部完全填充。

If insufficient grouting or empty areas are found, the grouting material should be added in time to ensure that the inside of the wall is completely filled.

- 配筋位置及数量，钻孔的孔径、深度和垂直度、植筋胶应满足设计及相关规范要求。

The location and quantity of reinforcement, the diameter, depth and verticality of the drilled holes, and the rebar glue should meet the design and relevant specifications.

- 固化养护：按照厂家提供的养护条件进行固化养护，固化期间禁止扰动。

Curing and curing: Curing and curing should be carried out according to the curing conditions provided by the manufacturer. No disturbance is allowed during the curing period.

- 在植筋固化后，按照设计及相关规范要求进行抗拔试验。

After the rebar is cured, the pull-out test should be carried out according to the design and relevant specifications.

抹灰及涂料工程Plaster and paint

用于抹灰及涂料工程的材料品种、规格、标号均应满足设计要求；乙方在确定供货厂家前，应向甲方递交样品，并提请甲方批准；在进场验收时，应向甲方提供符合南非国家现行质量标准的出厂合格证，否则，甲方有权拒绝验收或使用，由此造成的相关经济损失由乙方承担。

The types, specifications and grades of materials used for plastering and coating projects shall meet the design requirements. Before determining the supplier, the Party B shall submit samples to the Party A and seek approval from the Party A. During on-site acceptance, the Party B shall provide the Party A with a factory certificate that complies with the current South Africa national quality standards. Otherwise, the Party A has the right to refuse acceptance or use, and the relevant economic losses caused thereby shall be borne by the Party B.

    - 抹灰Plaster

- 抹灰前应将基层表面的尘土、污垢、油渍等清除干净，确保基层表面平整、干净。

Before plastering, the dust, dirt, oil stains, etc. on the surface of the base layer should be cleaned to ensure that the surface of the base layer is flat and clean.

- 对于混凝土表面，应凿毛或在表面洒水润湿后涂刷1:1水泥砂浆（加适量胶粘剂）。

For concrete surfaces, they should be roughened or the surface should be moistened with water and then coated with 1:1 cement mortar (with appropriate amount of adhesive).

- 对于砖砌体，应清除表面杂物、尘土，抹灰前应洒水湿润。

For brickwork, surface debris and dust should be removed and the surface should be moistened with water before plastering.

- 当抹灰总厚度大于或等于35mm时，应采取加强措施，加强措施应符合设计要求，如加强网的搭接宽度、锚固长度等。

When the total thickness of the plaster is greater than or equal to 35mm, reinforcement measures should be taken, and the reinforcement measures should meet the design requirements, such as the lap width and anchorage length of the reinforcement mesh.

- 室内墙面、柱面、门洞口和墙拐角处的阳角特殊处理，阴阳角、线条设置应符合规范要求。

Special treatment should be given to the external corners of interior walls, columns, door openings and wall corners, and the setting of internal and external corners and lines should comply with the specifications.

- 根据设计要求和实际情况选择合适的抹灰材料，抹灰材料应符合相关标准和规范。

Select appropriate plastering materials according to design requirements and actual conditions. The plastering materials should comply with relevant standards and specifications.

- 砂浆每层厚度宜应符合设计及南非本地相关标准及规范要求，在抹灰过程中，注意控制抹灰层的厚度，避免出现空鼓、裂缝等现象。

The thickness of each layer of mortar should comply with the design and relevant local standards and specifications of South Africa  . During the plastering process, pay attention to controlling the thickness of the plaster layer to avoid hollowing, cracks and other phenomena.

- 抹灰层完成后应及时进行养护，防止抹灰层过早干燥、开裂。养护方法可采用喷水、覆盖湿布等。

After the plaster layer is completed, it should be maintained in time to prevent the plaster layer from drying out and cracking prematurely. The maintenance methods can be spraying water, covering with wet cloth, etc.

- 分格缝设置：对于大面积抹灰，应合理设置分格缝，以减少裂缝的产生。分格缝的纵横间距不宜过大，一般不超过6m，且应在屋面转折处、与立墙的交接处等关键部位设置。

Setting of partition joints: For large-area plastering, partition joints should be set reasonably to reduce the occurrence of cracks. The vertical and horizontal spacing of partition joints should not be too large, generally not exceeding 6m, and should be set at key locations such as the roof turning point and the intersection with the vertical wall.

- 施工缝应留在分格缝、墙面阴角、落水管背后或独立装饰组成的边缘处，以便后续处理。施工缝处应确保抹灰层平整、无裂缝。

Construction joints should be left at partition joints, wall corners, behind downpipes or at the edges of independent decorative components for subsequent processing. The plaster layer at the construction joints should be flat and free of cracks.

- 对于已出现的接缝裂缝，应及时进行修补。修补前应先清除裂缝中的杂质，浇水湿润后，再按抹灰做法进行补缝。补抹的灰应与原有的灰结合严密、平直。

For cracks in joints that have appeared, they should be repaired in time. Before repairing, impurities in the cracks should be removed first, and after watering, the joints should be repaired according to the plastering method. The plaster to be repaired should be closely combined with the original plaster and be straight.

    - 涂料Paint

- 在施工前，应对涂料进行质量检查，确保无变质、结块等现象。检查涂料的颜色、粘度等是否符合要求。

Before construction, the paint quality should be checked to ensure that there is no deterioration, caking, etc. Check whether the color and viscosity of the paint meet the requirements.

- 清除基层表面上的灰尘、污垢、溅沫和砂浆流痕等杂物。使用清水或清洁剂清洗基层表面，确保无残留物。

Remove dust, dirt, splashes, mortar flow marks and other debris from the surface of the base. Use clean water or detergent to clean the surface of the base to ensure that there is no residue.

- 对基层上的缺棱掉角、孔洞、裂缝等缺陷进行修补。

Repair defects such as missing edges, holes, cracks, etc. on the base layer.

- 混凝土或抹灰基层在涂饰前应涂刷界面底漆。

The concrete or plaster base should be coated with interface primer before painting.

- 外墙涂料工程应分段进行，以分格缝、墙的阴角处或水落管等为分界线。

The exterior wall paint project should be carried out in sections, with partition joints, wall corners or downspouts as dividing lines.

- 控制涂层的厚度，避免过厚导致流坠、开裂等问题。

Control the thickness of the coating to avoid problems such as dripping and cracking caused by excessive thickness.

- 每层涂料的涂刷间隔应符合产品说明书的要求。

The interval between applying each layer of paint should comply with the requirements of the product instructions.

- 涂层均匀、平整、无漏刷、无透底现象。

The coating is even and smooth, with no missed spots and no bottom see-through.

- 检查涂层的颜色、光泽度等是否符合设计要求。

Check whether the color and glossiness of the coating meet the design requirements.

- 施工环境应清洁、通风、无尘埃。作业面环境温度满足涂料要求。

The construction environment should be clean, ventilated and dust-free. The ambient temperature of the working surface meets the requirements of the coating.

- 饰面工程的内外墙涂料颜色应符合设计要求或经甲方的指定。

The color of the interior and exterior wall paint and glazed tiles of the finishing works shall meet the design requirements or be specified by the Party A.

楼地面工程Floor

用于地面工程的材料应符合设计要求，或符合南非国家标准和行业规范的规定；乙方应递交样品供甲方选择；地面包括但不仅限于：防滑地砖、普通地砖、大理石地砖、耐酸砖、环氧地坪漆、防静电地板等。

The materials used for floor engineering shall meet the design requirements or comply with South Africa national standards and industry specifications; Party B shall submit samples for Party A to choose; the flooring includes but is not limited to: anti-slip floor tiles, ordinary floor tiles, marble floor tiles, acid-resistant bricks, epoxy floor paint, anti-static floor, etc.

    - 砖地面Tile floor

- 普通地砖、防滑地砖、大理石地砖、耐酸砖的规格及各项性能指标应满足设计要求，设计无要求时应符合南非国家标准或行业规范的规定。

Common floor tiles, anti-slip floor tiles, marble tiles and acid resistant tiles specifications and various performance indicators should meet the design requirements, and the design should meet the provisions of South Africa national standards or industry specifications when there are no requirements.

- 勾缝材料的选择要符合瓷砖的颜色和质地，避免勾缝后出现色差和不协调的情况。

The choice of grouting materials should be consistent with the color and texture of the tiles to avoid color difference and incoordination after grouting.

- 勾缝应密实、平整、光滑，无裂缝、空鼓和起砂现象。勾缝颜色应均匀一致，与瓷砖颜色相协调。

The grouting should be dense, flat, smooth, without cracks, hollows, and sanding. The grouting color should be uniform and consistent with the color of the tiles.

- 勾缝完成后，砖表面应平整、洁净、无污渍和划痕，接缝填嵌应密实、平直、宽窄一致。

After grouting, the tile surface should be flat, clean, free of stains and scratches, and the joint filling should be dense, straight, and uniform in width.

- 砖表面洁净，面层平整，阳角无翘曲，高度一致，结合牢固。

The tile surface is clean, the surface layer is flat, the external corners are not warped, the height is consistent, and the combination is firm.

    - 环氧地坪Epoxy Floor

- 环氧地坪漆的各项性能指标应满足设计要求，设计无要求时应符合南非国家标准或行业规范的规定；

The performance indicators of the epoxy floor paint shall meet the design requirements, and the design should meet the provisions of South Africa national standards or industry specifications when there are no requirements.

- 底层涂料由环氧树脂、固化剂组成，必须有效对抗水泥中碱和其他有害物质的渗出；在环氧树脂地面涂层材料涂装时，直接涂到地面基体上，起到封闭和粘结作用，底漆涂料不得与砼基层出现任何不相容问题；

The primer coating consists of epoxy resin and curing agent, which must be effective against the exudation of alkali and other harmful substances in cement; when the epoxy resin ground coating material is painted, it is directly applied to the ground substrate to play a closing and bonding role, and the primer coating must not have any incompatible problems with the concrete base.

- 底漆、中涂、面涂采用的原材料应保证每批配比一致，每批次无色差，且面漆具有抗污自洁功能，其环保性能必须符合南非国家标准。

The raw materials used for primer, middle coat and top coat should ensure the consistency of the ratio of each batch, no color difference in each batch, and the top coat has the function of anti-fouling and self-cleaning, and its environmental performance must meet the national standard of South Africa  .

- 面层无褶皱、鼓包、空鼓。

The surface layer has no wrinkles, bulges or hollows.

墙面工程decorative wall

    - 砖墙面Tile wall

- 墙砖铺贴前应进行浸泡处理，确保瓷砖充分吸水。

Tiles should be soaked before laying to ensure that the tiles fully absorb water.

- 铺贴时应使用专用粘结剂，确保瓷砖与基层粘结牢固。

Special adhesive should be used when laying to ensure that the tiles are firmly bonded to the base.

- 墙砖之间应留有适当的缝隙，以便后续填缝处理。

Appropriate gaps should be left between wall tiles to facilitate subsequent caulking.

- 通过敲击法检查墙面是否存在空鼓现象，发现空鼓应及时处理。

Check whether there are hollows on the wall by knocking. If any hollows are found, they should be dealt with in time.

- 检查墙面是否有裂缝产生，如有裂缝应进行修补。

Check the wall for cracks and repair them if any.

- 砖上墙时，必须使用瓷砖胶或瓷砖背胶增加粘结牢度，防止瓷砖脱落。

When installing vitrified tiles and other floor tiles on the wall, you must use tile glue or tile back glue to increase the bonding strength and prevent the tiles from falling off.

- 墙砖铺贴完成后应及时清理表面的脏污，确保瓷砖表面无划伤、缺棱掉角、裂纹现象。

After the wall tiles are laid, the dirt on the surface should be cleaned in time to ensure that there are no scratches, missing edges or cracks on the surface of the tiles.

    - 水泥基墙面Cementitous

- 基层应坚固、平整、无裂缝、无空鼓、无油污、无浮尘等缺陷。施工前应对基层进行清洁和修补处理。

The base should be firm, flat, without cracks, hollows, oil stains, floating dust and other defects. The base should be cleaned and repaired before construction.

- 采用合适的施工方法进行涂抹，涂层的厚度和均匀性满足设计要求。对于需要多层涂覆的涂料，应待前一层完全干燥后再进行下一层的施工。

Use appropriate construction methods to apply the coating, and the thickness and uniformity of the coating should meet the design requirements. For coatings that require multiple layers of application, the next layer should be applied only after the previous layer is completely dry.

- 施工完成后应及时进行养护，保持涂层湿润以促进水化反应的进行。养护时间根据产品说明书中的要求确定。

After the construction is completed, maintenance should be carried out in time to keep the coating moist to promote the hydration reaction. The curing time is determined according to the requirements in the product manual.

吊顶工程ceiling

- 吊顶工程的材料应符合设计要求，或符合南非国家标准和行业规范的规定；乙方应递交样品供甲方鉴定和选择，并经甲方认可后方可使用等。

The materials of the ceiling project shall meet the design requirements or conform to the provisions of South Africa national standards and industry codes; the Party B shall submit samples for the Party A's identification and selection and shall be approved by the Party A before use, etc.

- 扣板（装饰板）上的灯具、烟感器、喷淋头（若有）、风口篦子（若有）等设备位置应符合设计要求且美观，与扣板（装饰板）的交接应吻合、严密。

Fasteners (decorative panels) on the lamps, smoke detectors, sprinkler heads (if any), air vent grate (if any) and other equipment location should meet the design requirements and beautiful, and fasteners (decorative panels) should match the intersection, tight.

- 吊顶的标高、尺寸、起拱和造型应符合设计要求和国家现行有关标准规定。

The elevation, size, arch and shape of the suspended ceiling should comply with the design requirements and relevant national standards currently in force.

- 吊顶的平整度、垂直度等应符合相关标准要求。

The flatness and verticality of the suspended ceiling should meet the requirements of relevant standards.

- 灯具、风口、喷淋头等设备的安装位置应合理布局，与吊顶板材的交接应吻合严密。

The installation positions of lamps, vents, sprinkler heads and other equipment should be reasonably arranged, and the joints with the suspended ceiling panels should be closely matched.

- 重型灯具、电扇等重型设备严禁安装在吊顶龙骨上，应另设吊钩或其他支撑结构。

Heavy equipment such as heavy lamps and electric fans are strictly prohibited from being installed on the suspended ceiling keels. Hooks or other supporting structures should be installed separately.

- 各类龙骨和吊顶板材的质量应合格，无缺陷和破损现象。

The quality of various keels and suspended ceiling panels should be qualified, without defects and damage.

- 吊顶的安装质量应符合设计要求和相关标准规定。

The installation quality of the suspended ceiling should meet the design requirements and relevant standards.

- 吊顶内填充的吸声材料品种和铺设厚度应符合设计要求，并应有防散落措施。

The types and laying thickness of the sound-absorbing materials filled in the suspended ceiling should meet the design requirements, and anti-scattering measures should be taken.

- 吊顶施工应与其他工程（如水电、消防等）相互配合，确保整体工程的顺利进行。

The construction of the suspended ceiling should cooperate with other projects (such as water, electricity, fire protection, etc.) to ensure the smooth progress of the overall project.

- 按照设计及相关规范要求设置检修口。

Inspection openings shall be set up in accordance with the design and relevant specifications.

- 吊顶检修口两侧的轻钢龙骨平面位置、标高应正确，平行顺直。两次龙骨间距值误差不应超过+3mm，不宜有负偏差。C字型轻钢龙骨应背靠背安装，净距均等值极差应控制在1.5mm为宜。

The plane position and elevation of the light steel keels on both sides of the ceiling inspection opening shall be correct, parallel and straight. The error of the distance between two keels shall not exceed +3mm, and there should be no negative deviation. C-shaped light steel keels shall be installed back to back, and the net distance equalization value extreme difference shall be controlled within 1.5mm.

- 检修口的龙骨应有足够的检修面板滑行距离，即能够使整个吊顶检修口完全开启或闭合，便于维修与操作。

The plane position and elevation of the light steel keels on both sides of the ceiling inspection opening shall be correct, parallel and straight. The error of the distance between two keels shall not exceed +3mm, and there should be no negative deviation. C-shaped light steel keels shall be installed back to back, and the net distance equalization value extreme difference shall be controlled within 1.5mm.

- 检修口关闭后应具有良好的密封性能，防止灰尘、虫蚁等进入吊顶内部。

After the inspection opening is closed, it shall have good sealing performance to prevent dust, insects and ants from entering the interior of the ceiling.

电气设备安装工程Electrical equipment installation project

- 线管内线缆总截面积≤线管内径 40%，预留备用管线；强弱电分管、分槽，禁止同管混敷。

The total cross-sectional area of the cables in the conduit should not exceed 40% of the inner diameter of the conduit. Reserve additional pipeline space. Separate the power and signal cables in different conduits or troughs. It is prohibited to lay the power and signal cables together in the same conduit.

- 电缆敷设无扭曲、过度拉伸，转弯处预留松弛余量；设备端子处预留≥300mm 检修余量。

The cable laying is without any distortion or excessive stretching. A slack margin is reserved at the turning points; a maintenance margin of at least 300mm is reserved at the equipment terminals.

- 所有安装工程应符合以下规范要求：SANS 10142-1《建筑物布线规范》；配套 SANS 164（插头插座）、SANS 1507（PVC 电缆）、SANS 1339（XLPE 电缆）、SANS 10160（防雷）、SANS 61643（浪涌保护器 SPD）。

All installation works shall comply with the following specification requirements: SANS 10142-1 "Building Wiring Specifications"; along with SANS 164 (Plug and Socket), SANS 1507 (PVC Cable), SANS 1339 (XLPE Cable), SANS 10160 (Electrical Protection), and SANS 61643 (Surge Protective Device SPD).

暖通工程HVAC

- 根据设计要求确定风机的安装位置，确保满足设计要求。

Determine the installation position of the fan according to the design requirements to ensure that the design requirements are met.

- 根据设计及设备厂家要求固定风机，确保风机固定牢固可靠，避免在运行过程中发生位移或振动。

Fix the fan according to the design and equipment manufacturer's requirements to ensure that the fan is firmly and reliably fixed to avoid displacement or vibration during operation.

- 根据设计及厂家要求设置减震装置，减震装置的安装位置应正确，且各组或各个减震器承受荷载的压缩量应均匀一致。

Set up a shock absorber according to the design and manufacturer's requirements. The installation position of the shock absorber should be correct, and the compression amount of each group or each shock absorber under the load should be uniform and consistent.

- 风管的位置、标高和走向应符合设计要求，确保气流顺畅。

The position, elevation and direction of the air duct should meet the design requirements to ensure smooth airflow.

- 风管连接应严密、牢固，不得有漏风现象。

The air duct connection should be tight and firm, and there should be no air leakage.

- 连接处应采用密封胶密封，防止气体泄漏。

The joints should be sealed with sealant to prevent gas leakage.

- 支吊架的位置、间距应符合规范要求，确保风管稳固。

The position and spacing of the support brackets should meet the requirements of the specifications to ensure that the air duct is stable.

- 当风管穿越防火、防爆墙或楼板时，应设置预埋管或防护套管，并用柔性材料封堵。

When the air duct passes through fireproof, explosion-proof walls or floors, embedded pipes or protective sleeves should be installed and sealed with flexible materials.

- 穿越变形缝时，应设置伸缩节，确保风管在变形时不会损坏。

When crossing through deformation joints, expansion joints should be installed to ensure that the air duct will not be damaged during deformation.

- 风管保温材料的选择和厚度应符合设计要求。

The selection and thickness of the air duct insulation material should meet the design requirements.

- 安装完成后，应对风管系统进行压力测试，确保强度和严密性符合要求。

After installation, the duct system should be pressure tested to ensure that the strength and tightness meet the requirements.

- 调试运行前，应检查各阀门、调节装置等，确保正常工作。

Before commissioning, all valves, regulating devices, etc. should be checked to ensure normal operation.

- 百叶窗的安装位置应符合设计要求。

The installation position of the blinds should meet the design requirements.

- 检查百叶窗的固定方式应满足设计及相关规范要求。

Check that the fixing method of the blinds should meet the design and relevant specifications.

- 百叶窗的水平与垂直度满足设计及验收标准。

The horizontality and verticality of the blinds meet the design and acceptance standards.

- 风管与墙体、百叶窗与墙体、风机与墙体之间的密封应使用柔性材料，密封后墙面应美观。

The sealing between the duct and the wall, the blinds and the wall, and the fan and the wall should use flexible materials, and the wall surface should be beautiful after sealing.

屋面工程roof

用于屋面工程的材料应符合设计要求，或符合南非国家标准和行业规范的规定；乙方应递交样品供甲方鉴定和选择，并经甲方认可后方可使用；样品应包括防水卷材、挤塑保温板等。

Materials used for roofing works shall meet the design requirements or comply with the provisions of South Africa national standards and industry codes; the Party B shall submit samples for identification and selection by the Party A and shall be approved by the Party A before use; the samples shall include waterproofing membrane, extruded plastic insulation board, etc.

    - 防水卷材Waterproof membrane

- 铺贴防水卷材前,应先做好节点,附加层和屋面排水比较集中的部位的处理(屋面与水落口连接处及檐口、檐沟、天沟、屋面转角、板端缝等)，然后由屋面最低标高处向上施工，铺贴天沟、檐沟卷材时,宜顺着天沟、檐沟的方向,应尽量减少搭接，同时不得污染檐口外侧和墙面。防水卷材采用胶粘剂粘贴，用热熔或冷粘法贴于基层。

Before paving waterproofing membrane, it is necessary to deal with the joints, additional layers and the parts where the roof drainage is concentrated (the connection between the roof and the waterspout and the cornice, gutter, gutter, roof corner, plate end joint, etc.), and then construct upward from the lowest elevation of the roof. When paving the membrane of gutter and gutter, it is better to follow the direction of gutter and gutter, Overlap shall be minimized and the outside of cornice and wall shall not be polluted. The waterproof coiled material is pasted with adhesive and pasted on the base by hot melting or cold bonding method.

- 卷材多层铺贴时接逢应错开，铺贴时随着放卷随用喷枪往返均匀加热基层和卷材的交接处，喷枪距加热面适当，趁卷材的材面刚刚熔化时，将卷材向前滚铺、粘贴，完成后不得皱折、空鼓现象。阴阳角的处理如下：阴阳角处的基层做成R=50的圆弧，加铺一层卷材，阴角处以全粘实铺为主，阳角处以空铺为主，附加层的宽度为300mm。

The joints should be staggered when the coil is multi-layer paved. When the coil is laid, the spray gun should be used to evenly heat the junction between the base and the coil. The distance between the spray gun and the heating surface should be appropriate. When the surface of the coil is just melted, the coil should be rolled forward and pasted. After completion, there should be no wrinkle or hollowing. The treatment of internal and external corners is as follows: the base at the internal and external corners is made into R = 50 arc, and a layer of coiled material is added. The internal corners are mainly fully bonded, the external corners are mainly empty, and the width of the additional layer is 300 mm.

    - 淋（蓄）水试验 Water leakage test

淋水试验重点冲淋屋面的细部构造部位及山墙、女儿墙的泛水，注意天沟、水落口位置是否渗漏。蓄水试验蓄水应高出屋面最高点20㎜，静置时间不少于24h，不得有渗漏现象。

The water leakage test focuses on the detailed structural parts of the roof and the flashing of the gable and parapet, and pays attention to whether the gutter and water outlet are leaking. In the water storage test, the water storage shall be 20 mm higher than the highest point of the roof, and the standing time shall not be less than 24 hours, without leakage.

    - 屋面隔热层Roof insulation

- 屋面隔热层严禁在雨、雪和五级以上大风和天气施工，施工前要检查保温材料的含水率是否符合设计要求，铺设保温隔热层的基层表面应干燥、洁净、平整、无蜂窝、孔洞和裂缝。

It is strictly forbidden to construct the roof heat insulation layer in rain, snow, gale above level 5 and weather. Before construction, check whether the moisture content of the heat insulation material meets the design requirements. The surface of the base course for laying the heat insulation layer shall be dry, clean, flat, and free of honeycomb, holes and cracks.

- 粘结铺设板块状隔热层：板块状保温材料平粘在层面基层上，铺设前应满涂胶结材料，与基层之间相互粘牢。一般用水泥混合砂浆粘结，聚苯板材料应用沥青胶结材料。板缝间或缺角处应用碎屑加胶料拌匀填补严密。

Bonding laying plate-shaped insulation layer: plate-shaped insulation material is horizontally bonded on the base layer of the layer. Before laying, it shall be fully coated with cementitious material, which is firmly bonded with the base layer. Generally, cement mortar is used for bonding, and asphalt binder is used for polystyrene board. The gap or missing corner should be filled with crumbs and rubber.

    - 碎石及人行道砖Gravel and sidewalk brick

- 按照设计要求铺设人行道砖。

Lay sidewalk bricks according to the design requirements.

门窗工程door and windows

- 用于门窗工程的材料应符合设计要求，或符合南非国家标准和行业规范的规定；乙方应递交样品供甲方鉴定和选择，并经甲方认可后方可使用；样品应包括但不仅限于：木门、钢制防火门、木质防火门、钢制大门、铝合金门窗、铝合金百叶窗、铝合金卷闸门、闭门器、门锁、安装附件等。

The materials used for the door and window works shall meet the design requirements or comply with the provisions of South Africa national standards and industry codes; the Party B shall submit samples for identification and selection by the Party A and shall be approved by the Party A before use; the samples shall include but not limited to: wooden doors, steel fire doors, wooden fire doors, steel gates, aluminum alloy doors and windows, aluminum alloy shutters, aluminum alloy rolling doors, door closers, door locks, installation accessories, etc.

- 门窗的气密性、水密性、抗风性、保温性应符合设计要求，或符合南非国家标准和行业规范的规定。

The airtightness, watertightness, wind resistance and heat insulation of the doors and windows should meet the design requirements or conform to the provisions of South Africa national standards and industry codes.

- 平开门、双开门应有闭门器，其中双开门为顺序闭门器。

Swing doors, double doors should have closers, which double doors for sequential closers.

- 防火门的各项性能指标应符合设计要求，并满足南非国家国家标准或行业规范的规定。

The performance indicators of fire doors should meet the design requirements and the provisions of national standards or industry specifications of South Africa  .

给排水工程plumbing

- 用于本工程的管道规格、型号、阀门、水龙头、水泵、水表、配件等均应满足设计要求；乙方在确定供货厂家前，应向甲方递交样品，获得批准后方可采购；在进场验收时，应向甲方提供符合南非国家现行质量标准的出厂合格证，否则，甲方有权拒绝验收，由此造成的相关经济损失由乙方承担。

The pipe specifications, models, gate valves, taps, pumps, water meters, fittings, etc. used for the project shall meet the design requirements; the Party B shall submit samples to the Party A before determining the supply manufacturer and submit them to the Party A for approval; at the time of acceptance, the Party A shall be provided with the factory certificate of compliance with the current quality standards of South Africa  , otherwise, the Party A shall have the right to refuse acceptance or use, and the relevant economic losses caused shall be borne by the Party B.

- 管道安装，穿过屋面，楼板的管道应预埋套管，穿过墙壁的预留孔和暗管的墙槽，应在建筑工程施工时预先留好，穿过地下室外墙处应设防水套管。若在施工详图中未作规定，则可使用短钢管或铸铁管。管道在穿过混凝土伸缩缝处，应按设计图纸规定设置过缝措施。管子在安装前，应清除管内外污物。

Piping installation,The pipes passing through the roof and floor shall be embedded with casing pipes, the reserved holes passing through the wall and the wall grooves of concealed pipes shall be reserved in advance during the construction of construction projects, and the waterproof casing pipes shall be set at the places passing through the external wall of basement. If not specified in the construction details, short steel pipe or cast iron pipe can be used. When the pipe passes through the concrete expansion joint, the joint crossing measures shall be set according to the design drawings. The dirt inside and outside the pipe shall be removed before installation.

- 明装管道应按有关规范规定设管道支架。

Pipe supports shall be provided for surface mounted pipes according to relevant specifications.

- 水泵及水箱安装前基础已正式移交，有关轴线、标高线已画出，水泵基础混凝土强度达到设计要求，基础坐标、标高、尺寸、预留孔洞符合设计要求。

Before the installation of the water pump and water tank, the foundation has been formally handed over, the relevant axis and elevation lines have been drawn, the concrete strength of the water pump foundation meets the design requirements, and the foundation coordinates, elevation, size, and reserved holes meet the design requirements.

- 水泵及水箱基础表面应平整，清除油污、碎石、泥土、积水等。预埋地脚螺栓的螺纹和螺母应保护完好，放置垫铁部位表面应凿平。

The surface of the water pump and water tank foundation should be flat, and oil, gravel, soil, and water should be removed. The threads and nuts of the embedded anchor bolts should be well protected, and the surface of the pad iron should be chiseled flat.

- 水泵安装前应使用垫铁找正找平，且垫铁已固定，避免受力时松动。水泵找正找平后，装上地脚螺栓，螺杆应垂直，螺杆外露长度宜为螺杆直径的1/2。

Before installing the water pump, pad irons should be used for alignment and leveling, and the pad irons should be fixed to avoid loosening when under force. After the water pump is aligned and leveled, the anchor bolts are installed, the screw should be vertical, and the exposed length of the screw should be 1/2 of the screw diameter.

- 按设计要求及设备厂家要求设置隔振及减震措施。

Vibration isolation and shock absorption measures are set according to the design requirements and the requirements of the equipment manufacturer.

- 水泵与电机连接时，轴向倾斜和径向位移符合规定要求。

When the water pump is connected to the motor, the axial inclination and radial displacement meet the specified requirements.

- 进水管路应密封可靠，装有底阀的进水管应确保底阀轴线与水平面垂直安装，其轴线与水平面的夹角不得小于45°。

The water inlet pipeline should be sealed reliably, and the water inlet pipe equipped with a bottom valve should ensure that the bottom valve axis is installed vertically with the horizontal plane, and the angle between its axis and the horizontal plane shall not be less than 45°

- 将水箱放置在基础上，确保水箱端正、安装稳固，垂直度偏差每米不大于5mm。

Place the water tank on the foundation to ensure that the water tank is straight and firmly installed, and the verticality deviation is no more than 5mm per meter.

- 水箱各个接缝应平整、接口严密，无渗漏。水箱内部清洁，浮球阀启闭灵活、严密。

The joints of the water tank should be flat, the interface should be tight, and there should be no leakage. The inside of the water tank is clean, and the float valve is flexible and tight in opening and closing.

- 溢水管、泄水管不得与排水管道直接相连，应设有空气隔断。泄水及溢水应排放在排水地点附近，并设置防虫网罩。

The overflow pipe and the drain pipe shall not be directly connected to the drainage pipe, and an air partition shall be provided. The drain and overflow water shall be discharged near the drainage location, and an insect-proof net cover shall be set.

- 水箱表面应无划痕、无破损，面漆完整、光亮。

The surface of the water tank should be free of scratches and damage, and the topcoat should be complete and bright.

- 检查水箱的进出水、溢水、泄水等功能是否正常。

Check whether the water inlet and outlet, overflow, and drain functions of the water tank are normal.

照明工程lighting

- 用于本工程的照明灯具、开关插座等均应满足设计要求；The lighting fixtures, switches and sockets used in this project should meet the design requirements;

- 灯具及其配件齐全，无机械损伤、变形、油漆剥落和灯罩破裂等缺陷。T

he lamps and their accessories are complete and free of mechanical damage, deformation, paint peeling and cracked lampshades.

- 采用预埋吊钩、螺栓、螺钉、膨胀螺栓、尼龙塞或塑料塞固定，严禁使用木楔。Use embedded hooks, bolts, screws, expansion bolts, nylon plugs or plastic plugs for fixing. It is strictly forbidden to use wooden wedges.

- 安装位置与高度应满足设计要求及南非本地和国际标准。The installation position and height should meet the design requirements and South Africa local and international standards.

- 灯具及插座接线必须牢固，接触良好，避免通电打火现象。火线及零线应严格区分，线路尤其是预埋的线路或线管内严禁有接头。

The wiring of lamps and sockets must be firm and in good contact to avoid sparking when powered on. The live wire and the neutral wire should be strictly distinguished, and joints are strictly prohibited in the lines, especially the embedded lines or wire tubes.

- 布线时应先将导线拉直，按照横平竖直的原则进行布线，弯角处应严格安装成直角。When wiring, the wires should be straightened first, and the wiring should be carried out according to the principle of horizontal and vertical, and the corners should be strictly installed at right angles.

- 布线时应尽量减少交叉。

When wiring, crossover should be minimized.

- 导线颜色应按照规范选择。

The wire color should be selected according to the specifications.

- 线路安装完成后，应首先进行线路通断测试，确保所有线路连接正确无误。

After the line is installed, the line continuity test should be carried out first to ensure that all line connections are correct.

- 通电测试，按照负载顺序依次送电，检查灯具和开关插座的工作情况。

Then conduct a power-on test, supply power in order according to the load sequence, and check the working conditions of lamps and switches and sockets.

- 照明灯具的安装不仅要满足技术要求，还要注重美观性。灯具的布局和安装位置应与室内装饰风格相协调，营造出舒适和谐的室内环境。

The installation of lighting fixtures should not only meet technical requirements, but also pay attention to aesthetics. The layout and installation position of the lamps should be coordinated with the interior decoration style to create a comfortable and harmonious indoor environment.

- 蓄电池室及实验室的所有灯具、指示灯、线管及管件应满足防爆要求，卫生间的灯具、开关及插座应满足防水要求。

The lighting fixtures in the battery room should be explosion-proof, the lighting fixtures in the bathroom should be waterproof, and the wire pipes should meet the anti-corrosion requirements.

设备基础equipment foundation

- 设备基础标高、尺寸及位置的偏差应满足设计要求及设备厂家要求。

The deviation of the equipment foundation elevation, size and position shall meet the design requirements and the requirements of the equipment manufacturer.

- 基础外表面应无裂纹、空洞、掉角、露筋。

The outer surface of the foundation shall be free of cracks, voids, corner drop and exposed reinforcement.

- 基础表面和预留孔应清除干净，无油污、碎石、泥土、积水等。

The foundation surface and reserved holes shall be cleaned and free of oil, gravel, soil, water accumulation, etc.

- 预留孔洞内无露筋、凹凸等缺陷。

There shall be no exposed reinforcement, bumps and other defects in the reserved holes.

- 预埋件的位置、标高等应符合设计或规范要求。

The position and elevation of embedded parts shall meet the design or specification requirements.

- 基础混凝土表面的平整度满足设计及设备厂家要求，且误差在5mm以内。

The flatness of the foundation concrete surface meets the requirements of the design and equipment manufacturer, and the error is within 5 mm.

- 混凝土强度等级满足设计要求。

The concrete strength grade meets the design requirements.

- 根据设计要求设置沉降观测点。

Settlement observation points according to the design requirements.

- 二次灌浆前，乙方应按照设计及规范要求对混凝土表面凿毛、洒水湿润，并应向甲方提交设备基础二次灌浆申请，经甲方检查验收并批准后方可灌浆；灌浆材料的质量证明文件、试块取样等同混凝土浇筑。

Before secondary grouting, Party B shall roughen the concrete surface and wet it with water in accordance with the design and specification requirements, and shall submit an application for secondary grouting of the equipment foundation to Party A. Grouting can only be carried out after inspection and approval by Party A; the quality certification documents of the grouting materials and the sampling of test are the same as those for concrete pouring.

- 若涉及设备安装单位返移交的，应与设备安装单位办理设备基础返移交单，否则，甲方有权拒绝乙方的设备基础二次灌浆申请。

If the equipment installation unit is involved in the return and handover, the equipment foundation return and handover form shall be handled with the equipment installation unit. Otherwise, the Party A has the right to reject the Party B's application for secondary grouting of the equipment foundation.

厂区井及池General Manholes and Tanks

- 化粪池、检修井、雨水井、污水井按照设计图纸施工。

Septic tank, Manhole, handhole, rainwater wells and sewage tanks are constructed according to the design drawings.

- 化粪池应进行防水处理及防腐处理，排污管及排气管的安装位置应符合设计要求；化粪池盖材质规格及大小应满足设计及南非本地相关规范要求；盖板安装后严密。

The septic tank should be waterproofed and anti-corrosive treated, and the installation position of the sewage pipe and the exhaust pipe should meet the design requirements; the material specifications and size of the septic tank cover should meet the design and relevant South Africa local specifications; the cover should be tightly installed.

- 化粪池内防腐满足设计要求。

The anti-corrosion inside the septic tank meets the design requirements.

- 检修井、雨水井、污水井内部防水涂料满足设计要求。

The waterproof coating inside the inspection well, rainwater well and sewage well meets the design requirements.

- 按照设计及相关规范要求进行蓄水试验。

Carry out water storage test in accordance with the design and relevant specifications.

- 盖板及爬梯安装满足设计要求。

The installation of cover plates and ladders meets the design requirements.

- 进水标高、管道标高满足设计要求。

The water inlet elevation and pipeline elevation meet the design requirements.

电缆沟及排管Cable trench and duct bank

- 根据设计要求选择合适的管材，并对管材进行质量检查，确保无裂痕、破损等现象。

Select appropriate pipes according to design requirements and conduct quality inspections on the pipes to ensure that there are no cracks, breakages, etc.

- 管道安装前应进行清扫和冲洗，确保管内无杂物。

Before installing the pipes, they should be cleaned and flushed to ensure that there is no debris in the pipes.

- 管道安装过程中应控制管道的中线位置和高程，确保管道安装平直、稳固。

During the installation of pipe, the centerline position and elevation of the pipes should be controlled to ensure that the pipes are installed straight and stable.

- 多层排管铺设时，上下接头应错开布置，防止断裂。

When laying multi-layer pipes, the upper and lower joints should be staggered to prevent breakage.

- 管道安装完成后，应根据设计要求进行固定和保护等。

After the pipes are installed, they should be fixed and protected according to design requirements.

- 电缆排管混凝土浇筑时避免碰撞管道，造成管道移位。

When pouring concrete for cable pipes, avoid colliding with the pipes to cause the pipes to shift.

- 电缆沟的位置、尺寸等满足设计要求。

The position and size of the cable trench meet the design requirements.

- 电缆沟的预埋件应进行可靠固定，材质满足设计要求。允许安装偏差：中心线位移 ≤10mm；埋入深度偏差≤5mm；垂直度偏差 ≤5mm。

The embedded parts of the cable trench should be reliably fixed and the material should meet the design requirements. Allowable installation deviation: centerline displacement ≤10mm; embedment depth deviation ≤5mm; verticality deviation ≤5mm.

- 电缆沟盖板安装应平整，高低差满足设计及相关规范要求，电缆沟密封材料应防水、防晒、防火，密封后整体美观。

The cable trench cover should be installed flat, and the height difference should meet the design and relevant specifications. The cable trench sealing material should be waterproof, sun-proof and fire-proof, and the overall appearance should be beautiful after sealing.

建筑防雷及接地earthing and lightning

- 建筑防雷及接地材料按设计要求选用，并应符合设计及南非标准或行业规范的规定；均应在采购前提供样品给甲方审核，经甲方审查同意后方可采购。

The lightning protection and grounding materials for buildings shall be selected according to the design requirements and shall comply with the design and South Africa  n standards or industry specifications. Samples shall be provided to the Party A for review before procurement, and procurement shall be carried out only after the Party A's review and approval.

- 避雷针、避雷带、避雷网安装位置应正确，安装方式应符合设计要求。焊接固定的焊缝应饱满无遗漏，螺栓固定的应防松零件齐全，焊接连接处应防腐完好。

The installation position of lightning rods, lightning strips, and lightning protection nets shall be correct, and the installation method shall comply with the design requirements. The welds of welded fixation shall be full and without omissions, the bolted fixation shall have complete anti-loose parts, and the welded joints shall be well protected against corrosion.

- 引下线应沿建筑物四周均匀或对称布置，其平均间距应符合设计及南非标准或行业规范的规定。

The down conductors shall be arranged evenly or symmetrically around the building, and their average spacing shall comply with the design and South Africa  n standards or industry specifications.

- 防腐处理：明敷的引下线应平直、无急弯，并应设置专用支架固定，引下线焊接处应刷油漆防腐且无遗漏。

Anti-corrosion treatment: The exposed down conductors shall be straight and without sharp bends, and shall be fixed with special brackets. The welding parts of the down conductors shall be painted for anti-corrosion and without omissions.

- 接地装置埋设深度符合设计及南非标准或行业规范的规定。

The buried depth of the grounding device shall comply with the design and South Africa  n standards or industry specifications.

- 接地装置在施工完毕后，应测试接地阻值，并必须符合设计要求。

After the construction of the grounding device is completed, the grounding resistance shall be tested and must comply with the design requirements.

- 所有用于防雷保护的金属构件均应可靠焊接，形成电气通路，并做好防腐处理。

All metal components used for lightning protection shall be reliably welded to form an electrical path and be well protected against corrosion.

其他设施Other facilities

其他设施包括但不限于：防撞柱、碎石、绿化、护坡、排水坡道、项目标志牌。

Other facilities include but are not limited to: crash barriers, gravel, Landscaping, embankment, drainage ramps, and project signs.

    - 防撞柱Crash barrier

- 防撞柱应选用坚固耐用的材料，以确保其在车辆碰撞时能够承受较大的冲击力而不易损坏。

Anti-collision columns should be made of strong and durable materials to ensure that they can withstand large impact forces without being easily damaged when vehicles collide.

- 所选材料应具有一定的抗冲击能力、耐腐蚀性和耐候性，以适应不同环境条件下的使用需求。

The selected materials should have certain impact resistance, corrosion resistance and weather resistance to meet the use requirements under different environmental conditions.

- 防撞柱应具有一定的高度和直径，具体尺寸需根据实际应用场景和保护对象来确定，以确保其在车辆碰撞时能够有效地起到保护作用。

Anti-collision columns should have a certain height and diameter. The specific size should be determined according to the actual application scenario and the object to be protected to ensure that they can effectively play a protective role when vehicles collide.

- 防撞柱的形状设计应考虑其稳定性和抗冲击性能。

The shape design of anti-collision columns should take into account their stability and impact resistance.

- 防撞柱安装位置及间距应满足设计要求。

The installation position and spacing of anti-collision columns should meet the design requirements.

- 防撞柱应采用可靠的固定方式安装在地面或建筑结构上，以确保其在受到冲击时不会松动或移位。

Anti-collision columns should be installed on the ground or building structure in a reliable way to ensure that they will not loosen or shift when impacted.

- 防撞柱应进行明显的标识，以提醒驾驶员注意避让，并避免发生碰撞事故。

Anti-collision columns should be clearly marked to remind drivers to avoid and avoid collision accidents.

- 可采用明亮的颜色和反光材料制作标识和警示设施，以确保在不同光线条件下都能够清晰可见。

Bright colors and reflective materials can be used to make signs and warning facilities to ensure that they can be clearly seen under different lighting conditions.

- 防撞柱的设计和制造应符合相关的国家和行业标准规范，以确保其质量和安全性。

The design and manufacture of anti-collision columns should comply with relevant national and industry standards and specifications to ensure their quality and safety.

- 在制造过程中，应严格控制材料和加工工艺的质量，确保防撞柱能够承受一定的冲击力而不变形或损坏。

During the manufacturing process, the quality of materials and processing technology should be strictly controlled to ensure that the anti-collision column can withstand a certain impact force without deformation or damage.

    - 碎石Gravel

- 碎石的尺寸满足设计要求。

The size of the gravel meets the design requirements.

- 碎石铺设前铺设满足设计要求的土工布。

Before laying the gravel, a geotextile that meets the design requirements is laid.

- 铺设的厚度满足设计要求。

The laying thickness meets the design requirements.

    - 绿化

- 树苗应满足满足设计及甲方要求。

The seedlings should meet the design and Party A's requirements.

- 开挖前需了解地下设施等隐蔽物埋设情况，并经甲方同意后施工，避免破坏。

Before excavation, it is necessary to understand the location of underground facilities and other hidden objects, and start construction after obtaining Party A's consent to avoid damage.

- 种植坑的大小需根据苗木根系、土球大小确定，深度满足要求。

The size of the planting pit should be determined according to the root system of the seedlings and the size of the soil ball, and the depth should meet the requirements.

- 种植时应保持苗木直立，不得倾斜，土球外包裹的包装物需拆除。

When planting, the seedlings should be kept upright and not tilted, and the packaging wrapped around the soil ball should be removed.

    - 护坡Embankment

- 在砌筑开始前，进行测量放样，确定护坡的准确位置和尺寸。

Before the start of masonry, measurement and setting out should be carried out to determine the exact position and size of the slope protection.

- 对坡面进行修整，确保坡面平整，无松动土层和冲沟。

The slope surface should be trimmed to ensure that it is flat and free of loose soil and gullies.

- 砌筑时应从底部向上进行，错缝竖砌，单层砌筑，坡脚与封边均应使用较大块石料。

Masonry should be carried out from the bottom to the top, with staggered vertical masonry and single-layer masonry. Larger stones should be used for the foot of the slope and the edge sealing.

- 砌石与岸坡接触处应开挖成适合块石形状，使块石与岸坡结合紧密。

The contact between the masonry and the slope should be excavated into a suitable shape for the stone blocks so that the stone blocks are tightly combined with the slope.

- 护坡面砌缝的宽度不应大于25mm，砌石边缘应顺直、整齐牢固。

The width of the masonry joints on the slope protection surface should not be greater than 25 mm, and the edges of the masonry should be straight, neat and firm.

- 砌体外露面的坡顶和侧边应选用较整齐的石块砌筑平整，不得在外露面用块石砌筑而中间以小石填心。

The top and sides of the exposed surface of the masonry should be built flat with relatively neat stones. It is not allowed to use stone blocks on the exposed surface and fill the middle with small stones.

- 为使砌石块的全长有坚实支撑，所有前后的明缝均应用小片石料填塞紧密。

In order to ensure that the entire length of the stone blocks has solid support, all front and rear open joints should be tightly filled with small pieces of stone.

- 砌筑过程中应适时进行压实处理，确保石块之间紧密接触。

Compaction should be carried out in a timely manner during the masonry process to ensure close contact between stones.

- 砌筑完成后应进行养护，防止石块松动或开裂。

After the masonry is completed, maintenance should be carried out to prevent the stones from loosening or cracking.

- 对进场的石料进行质量检查，确保石料符合设计要求。

The quality of the stones entering the site should be checked to ensure that the stones meet the design requirements.

- 在砌筑过程中进行定期检查，确保砌筑质量符合标准。

Regular inspections should be carried out during the masonry process to ensure that the masonry quality meets the standards.

    - 排水坡道Drainage ramp

- 排水坡道的位置、尺寸及坡度满足设计及相关标准。

The location, size and slope of the drainage ramp meet the design and relevant standards.

- 排水坡道涂刷环氧沥青，环氧沥青厚度满足设计要求。

The drainage ramp is painted with epoxy asphalt, and the thickness of the epoxy asphalt meets the design requirements.

    - 项目标识牌Project sign

- 标识牌上的信息必须准确、清晰,文字排版应合理，大小适中，颜色对比鲜明，确保在各种环境条件下都能被清晰识别。

The information on the sign must be accurate and clear, the text layout should be reasonable, the size should be moderate, and the color contrast should be clear to ensure that it can be clearly identified under various environmental conditions.

- 图像和符号的选择应直观易懂，与所指示的内容紧密相关，避免产生歧义。

The selection of images and symbols should be intuitive and easy to understand, closely related to the content indicated, and avoid ambiguity.

- 标识牌的材料应具有良好的耐用性，能够抵抗日晒、雨淋、风吹等自然因素的侵蚀，确保长期使用不褪色、不变形。

The material of the sign should have good durability, be able to resist the erosion of natural factors such as sun, rain, and wind, and ensure that it will not fade or deform after long-term use.

- 制作过程中应确保标识牌的尺寸、形状、文字、图像等要素精确无误，符合设计要求。

During the fabrication, the size, shape, text, image and other elements of the sign should be accurate and meet the design requirements.

- 标识牌的表面应平整光滑，无气泡、裂纹、毛刺等缺陷。文字、图像等要素应清晰可辨，无模糊、断缺等现象。

The surface of the sign should be flat and smooth, without defects such as bubbles, cracks, and burrs. Elements such as text and images should be clearly distinguishable without blurring, breaking, etc.

- 标识牌的安装应牢固可靠，能够承受一定的风力和其他外力作用而不发生倾倒或脱落。

The installation of the sign should be firm and reliable, and can withstand certain wind and other external forces without tipping or falling off.

- 标识牌的安装位置应合理选择，确保观察者能够在需要时方便地看到并理解其指示的内容。同时，应避免安装在遮挡物后面或视线盲区等位置。

The installation location of the sign should be reasonably selected to ensure that the observer can easily see and understand the content of its instructions when needed. At the same time, it should be avoided to install it behind obstructions or in blind spots.

现场管理Site Management

  - 现场施工和总平面管理Site Construction General Layout Management

- 应严格按照施工总平面布置图进行施工平面管理，明确责任区负责人及安监负责人，各区的平面管理应服从总平面图的要求和规划，并履行报批手续。乙方进入另一个乙方的责任区内施工，必须服从责任区单位的管理，并办理进出厂手续，经责任区单位签字同意后方可实施。

The construction plane management shall be carried out in strict accordance with the general construction layout plan, and the person in charge of the responsible area and the person in charge of safety supervision shall be specified. The plane management of each area shall comply with the requirements and planning of the general layout plan, and the approval procedures shall be performed. The Party B entering into another Party B's responsibility area for construction must obey the management of the unit in the responsibility area and go through the procedures for entering and leaving the factory, which can be implemented only after being signed and approved by the unit in the responsibility area.

- 总平面布置应严格按照甲方提供的区域进行布置，乙方应根据甲方给出的区域进行详细规划，包括建造要求，报甲方审定后实施。中途不得随意改变，若有更改应提出书面申请，得到甲方的同意后进行。

The general layout shall be arranged in strict accordance with the area provided by the Party A, and the Party B shall make detailed planning according to the area provided by the Party A, including the construction requirements, which shall be submitted to the Party A for approval before implementation. It is not allowed to change at will in the middle of the process. If there is any change, a written application shall be made and it shall be carried out with the consent of the Party A.

- 乙方不得占用或有限制道路通畅的举措，如确实需要是应提前一周提出书面申请，明确地点及所需时间，经甲方同意后，在批准的时间内实施。

The Party B shall not occupy or restrict the unobstructed road. If it is really necessary, it shall submit a written application one week in advance, specify the location and time required,and implement it within the approved time after the approval of the Party A.

- 每个单位工程开工前，乙方应在单位工程施工组织设计中明确区域划分情况，并报甲方批准后实施。

Before the commencement of each unit project, the Party B shall make clear the area division in the construction organization design of unit project, and report to the Party A for approval before implementation.

- 办公临建设施完整、环境清洁。生产临建整洁、布置整齐，安全管理责任、制度、规定到位。

The temporary office facilities are complete and the environment is clean. The temporary production buildings shall be clean and tidy, and the safety management responsibilities, systems and regulations shall be in place.

- 各责任区应严格执行有关的环境卫生标准要求。每个作业面都应作到“工完料尽场地清”，剩余材料要堆放整齐，废料及时清理。

Each responsible area shall strictly implement the requirements of relevant environmental health standards. Each working surface shall be made to "clean up the site after the completion of work", the remaining materials shall be stacked neatly, and the waste materials shall be cleaned in time.

- 乙方应做好施工场地地下管线及沟道和邻边建筑物、构筑物的保护工作，大件运输通过或停放之处有地下沟管设施时乙方要做好执掌加固措施，方案报甲方批准后方能实施。在施工中对地下沟管设施和邻近建筑物造成损坏的，由乙方赔偿损失。

The Party B shall well protect the underground pipeline, ditch, adjacent buildings and structures at the construction site. When there are underground ditch facilities at the place where large-scale transportation passes or parking, the Party B shall take charge of the reinforcement measures, and the method can be implemented only after it is approved by the Party A. In case of damage to underground ditch and pipe facilities and adjacent buildings during construction, the Party B shall compensate for the loss.

- 施工中发现影响施工的地下障碍物时，乙方应于最短的时间内以书面形式通知甲方，同时提出处置方案。甲方收到处置方案后24小时内予以认可或提出修正方案。甲方承担由此发生的费用。所有现在的地下障碍物有归属单位时，甲方应报请有关部门协同处置。

When underground obstacles affecting construction are found during construction, the Party B shall inform the Party A in written form within the shortest time and propose disposal plan. The Party A shall approve or propose amendment method within 24 hours after receiving the disposal method. The Party A shall bear the expenses incurred therefrom. When all existing underground obstacles have their own units, the Party A shall report to relevant departments for collaborative disposal.

- 乙方服从甲方的现场用电、用水、机械管理，如其他包商需要使用乙方的资源， 各乙方应首先自行协调，每个乙方有配合其他乙方工作的义务，服从甲方的统一协调，所使用资源的价格按照市场价格。

The Party B shall obey the on-site electricity, water and mechanical management of the Party A. If others need to use the Party A’s resources, all Party B shall first coordinate themselves. Each Party B has the obligation to cooperate with other Party B and obey the Party A’s The unified coordination, the price of the resources used is in accordance with the market price.

  - 施工用水 Construction Water

施工及消防用水的储水设施、水源提供及管网均由乙方负责，乙方根据现场实际需要编制施工及消防用水规划并提交甲方批准后执行，用水及排水必须符合南非本地的环保要求。

The Party B shall be responsible for the storage facilities, water supply and pipe network of construction and fire fighting water. The Party B shall prepare construction and fire fighting water plans according to the actual needs of the site and submit to the Party A for approval before implementation.The water and drainage shall meet the local environmental requirements of South Africa  .

  - 施工电源 Construction Power

施工现场用的发电设施、配电设施、电缆、接地及计量器具均由乙方负责，乙方根据现场实际需要编制用电实施规划并提交甲方批准后执行，电缆及配电设施必须满足用电安全规程规范、安全设施标准化（满足CEEC标准化要求）、安全文明施工策划等管理规定的要求。乙方应根据其标段的实际施工用电情况自行准备施工备用电源，满足施工需求。

The Party B shall be responsible for the power generation facilities, power distribution facilities, cables, grounding and measuring instruments. The Party B prepares the power consumption implementation plan according to the actual needs of the site, and submits to the Party A for approval before implementation. The cables and power distribution facilities must meet the Electricity safety regulations, standardization of safety facilities (Meet the CEEC standardization requirements), safety and civilized construction planning and other management regulations. The Party B shall prepare the construction backup power supply by itself according to the actual construction power consumption of its bidding section to meet the construction needs.

  - 施工人员管理Construction  personnel management

- 乙方进入施工现场必须穿戴甲方规定统一的工作服，决策层、管理层、作业层及安监人员必须有明显的穿戴区别。

The Party B must wear uniform work clothes specified by the Party A when entering the construction site, and the decision-making level, management level, operation level and safety supervision personnel must have obvious wearing differences.

- 乙方的施工人员必须服从甲方的统一管理、调配及协调，严格执行甲方制定的相关管理制度。

The Party B's construction personnel must obey the unified management, deployment and coordination of the Party A, and strictly implement the relevant management system formulated by the Party A.

- 乙方施工人员进出大门必须有工作卡，经门岗电脑验证方可进入。

The Party B's construction personnel must have a work card for entering and leaving the gate, and can enter only after being verified by the gate post computer.

- 乙方的施工车辆进入工地应有甲方发给的专用出入通行证或持乙方指定人员签发的临时通行证，乙方的车辆离开工地现场时应配合门岗的检查，不得携带任何物资设备出场，如确须携带出场时应有乙方的工地负责人或指定人员的批条，批条应注明出场物资设备的数量规格及出场车辆的车牌号码，并经甲方指定负责人签认后，由门岗确认方可出场。

The Party B's construction vehicles entering the construction site shall have a special access pass issued by the Party A or a temporary pass issued by the Party B's designated personnel. When leaving the construction site, the Party B's vehicles shall cooperate with the inspection of the gate post, and shall not bring any materials and equipment out of the site. If it is necessary to bring out of the site, the Party B's person in charge of the construction site or the designated personnel's approval shall be provided. The approval shall indicate the items to be delivered out of the site The quantity and specification of the equipment and the license plate number of the vehicles leaving the site shall be signed and confirmed by the person in charge designated by the Party A, and then they can leave the site after being confirmed by the gate post.

- 进入施工的员工必须持有齐全的有效的相关证件，否则所处出现的问题由乙方负责。

The employees entering the construction must have complete and effective relevant certificates, otherwise the Party B shall be responsible for the problems.

- 乙方应遵守当地政府有关主管部门关于施工场地交通、施工噪音以及安全生产等的管理规定，按规定办理有关手续，并以书面形式通知项目法人，因乙方的责任造成的罚款由乙方承担。

The Party B shall comply with the management regulations of the relevant competent department of the local government on the traffic, construction noise and safety production of the construction site, go through the relevant procedures as required, and notify the project legal person in written form. The Party B shall bear the penalty caused by the Party B's responsibility.

  - 施工准备Construction Preparation

    - 总体要求 General requirements

现场开工前的施工准备包括但不限于以下内容：

Construction preparation before site commencement includes but not limited to:

- 乙方应根据甲方发颁发的项目管理规章制度建立相应的管理制度并提交甲方审核批准；

The Party B shall establish the corresponding management regime according to the project management plan and regulations issued by the Party A and submit to the Party A for review and approval.

- 乙方要上报专业分包单位和建筑材料的供应商的资格，包括资质等级、业绩、财务状况及项目经理等信息，经甲方批准。材料要满足主合同规定的厂家、品牌要求；

The Party B shall submit the qualification of professional Party Bs and suppliers of construction materials, including qualification level, performance, financial status, project manager and other information to the Party A for approval. The materials shall meet the requirements of manufacturers and brands specified in the main contract.

- 为确保节点和施工顺利实施，乙方必须提交满足进度要求的详细图纸需求计划和施工进度计划并满足甲方的里程碑节点要求；

In order to ensure the smooth implementation of node and construction, the Party B must submit the detailed drawing demand plan and construction schedule meeting the milestone requirements.

- 根据甲方提供的相关技术资料（勘察报告、施工图纸等），充分考虑建设地的地质条件、社会环境和工程特征等编制施工方案，报甲方和业主审核批准；

According to the relevant technical documents (survey report, construction drawings, etc.) provided by the Party A, fully consider the geological conditions, social environment and engineering characteristics of the construction site, prepare the construction method, and submit it to the Party A and the owner for review and approval;

- 根据业主和南非当地政府的要求，配合甲方提供办理施工许可的相关资料，约定由乙方负责的施工许可和执照由乙方办理并提交甲方备案；

According to the requirements of the owner and the government of South Africa  , cooperate with the Party A to provide relevant documents for the construction permit. The construction permits and licenses for which the Party B is responsible shall be handled by the Party B and submitted to the Party A for the record;

- 乙方需要提交工程开工报告给甲方及业主审核批准；

The Party B shall submit the project commencement report to the Party A and the owner for approval

- 项目HSE管理要求需要办理的相关作业许可；

Relevant operation permits required by HSE management of the project;

    - 人员准备Personnel preparation

- 乙方应根据施工总体计划，配置相关施工作业人员，并明确各个岗位职责及其组织内部指令传递和沟通方式。当乙方施工进度不满足现场实际需求时，EPC项目部有权要求乙方增加相关施工人员，乙方不得拒绝。

The Party B shall allocate relevant construction workers according to the overall construction plan, and define the responsibilities of each position and the internal instruction transmission and communication methods of the organization.When the Party B's construction schedule fails to meet the actual requirements of the site, EPC Project Department has the right to require the Party B to add relevant construction personnel, and the Party B shall not refuse.

- 起重机操作、起重指挥、电气及焊接作业人员等特种作业人员应持有效的特种作业操作证，报审并经EPC项目部认可。

Special operators such as crane operation, hoisting command, electrical and welding operators shall hold valid special operation certificate and submit it for examination and approval by EPC Project Department.

- 所有施工人员应参与EPC项目部组织的相关作业的安全、技术等培训，培训合格后取得上岗资格。

All construction personnel shall participate in the training on safety and technology of relevant operations organized by EPC project Department, and obtain the post qualification after passing the training.

- 参加施工人员需参加各级安全技术交底，熟悉并掌握相关作业内容、流程和具体要求。

Construction personnel shall participate in safety technology disclosure at all levels, and be familiar with and master relevant operation content, process and specific requirements.

    - 机工具准备Machine tool preparation

- 安装施工所使用的工具应经项目部HSE部门进行检验，检验合格者方可在本工程施工中使用。

The tools used in installation and construction shall be inspected by HSE Department of the project Department. Only those who pass the inspection can be used in this project construction.

- 乙方首先应该保证他们提供的工机具是在有效的检验周期内，由符合南非要求的校验机构提供校验证明,并进行定期校验。

The Party B shall first ensure that the machinery and tools provided by them are in the effective inspection cycle, Verification certificate provided by the calibration body meeting South Africa requirements, and conduct regular verification.

- 本工程使用的计量仪器（游标卡尺、经纬仪、扭矩扳手、钢尺）应校验检测，并在有效期内，检验合格者方可使用。

The measuring instruments (vernier caliper, theodolite, torque wrench and steel ruler) used in this project shall be checked and tested, and shall be used only after passing the inspection within the validity period.

- 作业使用的起重机等机械设备的型号、工况、配置（包括附件）、技术性能等应符合项目施工组织设计、施工方案中的有关技术要求。

The model, working condition, configuration (including accessories) and technical performance of the crane and other mechanical equipment used in the operation shall meet the relevant technical requirements in the construction organization design and construction scheme of the project.

- 所有吊装锁具和工器具应具有产品合格证明文件，且经入场检验合格后方可投入使用。吊索具在使用前应检查是否存在缺陷，规格型号是否与施工方案相符。

All lifting locks and tools should have the product qualification certificate, and pass the admission inspection before being put into use.Before use, check whether the sling has defects and whether the specifications and models are in accordance with the construction plan.

- 手持电动工具在一般场所宜选用II类工具，在潮湿场所和金属构架上作业应选用III类工具。焊接设备应放置在防雨、干燥通风处，并接地良好。

Hand-held power tools should be class II tools in general, and Class III tools should be used in damp places and on metal frames.Welding equipment should be placed in a rainproof, dry and ventilated place and well grounded.

    - 材料准备Stores reserve

- 材料到货后必须对设备进行清点数量和检查质量，质量不合格者不得使用，并提供不合格清单。

After the arrival of the materials, check the quantity and check the quality of the equipment. The unqualified quality shall not use it, and the list of unqualified shall be provided.

- 对于易丢失的材料，比如安装用的螺栓、垫圈、紧固件必须清点齐全，同时注意螺栓种类的不同。

For the materials that are easy to lose, such as the bolts, washers and fasteners used for installation, they must be complete, and pay attention to the different types of bolts.

- 清点构件的数量，核实实物与材料清单、组装图是否相符，并做好缺料余料的填表登记，及时上报项目部。

Count the number of components, verify whether the material objects are consistent with the material list and assembly drawing, fill in the form of missing and surplus materials and timely report to the project department.

- 对于有特殊要求的部件，比如镀锌构件，构件应镀锌完好，如因运输造成局部镀锌层磨损时，应涂上厂家提供的防锈涂料，进行防锈处理。涂刷前，应将磨损处清洗干净保持干燥。

For parts with special requirements, such as galvanized members, the members shall be galvanized, If the local galvanizing layer is damaged due to transportation, apply the anti-rust coating provided by the manufacturer for anti-rust treatment. Before brushing, should be the wear place clean to keep dry.

- 设备应按技术文件要求分类、分区存储，存储场地应保持清洁、通风及干燥，并定期检查。

The equipment should be classified and stored in different areas according to the requirements of technical documents. The storage site should be kept clean, ventilated and dry, and checked regularly.

    - 技术准备Technical preparation

- 安装施工前，必须对全体施工人员进行技术交底，安装相关的安全技术措施应落实。

Before installation and construction of the bracket, technical disclosure must be made to all construction personnel, and installation related safety and technical measures should be implemented.

- 施工人员熟悉施工图纸，并熟悉了解施工图纸和技术规范。

Construction personnel are familiar with the construction drawings, and understand the construction drawings and technical specifications.

- 安装过程中需做好偏差记录表格，偏差记录表见ITP相关标准。

During installation, the deviation record form shall be prepared, see the relevant standard in ITP.

- 乙方在中标后3周内提交施工组织设计方案，临建方案，全厂定置化平面图。

The Party B shall submit the construction organization design plan, temporary construction method statement and the whole plant customized layout drawing within 3 weeks after winning the bid.

- 乙方在中标后2周内提交项目文件清单及完成日期。

The Party B shall submit the list of project documents and the date of completion within 2 weeks after winning the bid

    - 作业环境working environment

- 施工期间现场应定制化布置，保持场地和道路畅通，清除影响材料转移和施工的障碍。

During construction, the site should be customized to keep the site and road unblocked and remove obstacles affecting material transfer and construction.

- 现场布置应符合安全文明施工要求，材料堆放整齐，现场设置施工标志牌和安全警示牌等。

The site layout shall meet the requirements of safe and civilized construction, the materials shall be stacked neatly, and the construction signs and safety warning signs shall be set up on the site.

- 作业区域应无存在隐患的电气线路及其它高温发热、易燃易爆、腐蚀性化学物品。

The working area should be free from hidden electrical circuits and other high-temperature, inflammable, explosive and corrosive chemicals.

- 配合甲方迎接上级领导及上级单位的检查工作，包括乙方施工区域的文明施工、公共区域的文明施工等；以甲方统一要求及责任划分为准。

Cooperate with Party A to welcome the inspection of superior leaders and superior units, including civilized construction in Party B’s construction area and civilized construction in public areas, etc.; the unified requirements and division of responsibilities of Party A shall prevail.

    - 机械管理Machine Management

- 本标段所有机械、机工具均由乙方负责并承担相应费用，进场机械无论是乙方自有或租赁都必须经过甲方或业主的审核审批并检验合格后方可进场作业，相关人员必须具备有关部门颁发的上岗资格证；所需要的起重工及起重索具等由乙方负责。机械退场时要办理退场手续，并取得甲方和业主的同意才能退场。

The Party B shall be responsible for and bear the corresponding costs for all the machinery and tools in this bid section. The mobilized machinery, whether owned or leased by the Party B, must be reviewed, approved and inspected by the Party A or the owner before entering the site for operation. The relevant personnel must have the qualification certificate issued by the relevant departments. The Party B shall be responsible for the required lifting workers and lifting slings. When the machinery leaves the site, it is necessary to go through the exit formalities and obtain the consent of the Party A and the owner before leaving the site.

- 乙方以甲方名义进(出)口的工机具、材料等必须单证相符且符合南非当地海关法律法规，若出现单证不符或被海关扣押则由乙方自行处理，由此导致设备清关延误产生的滞港费和仓储费由乙方承担。

The Party B's machinery, materials, etc. imported (exported) in the name of the Party A must conform to the documents and comply with the laws and regulations of the local customs of the South Africa  . If the documents do not conform or are seized by the customs, the Party B shall deal with them by itself, and the demurrage fee and storage fee caused by the delay in customs clearance of the equipment shall be borne by the Party B. If the documents do not conform to the laws and regulations.

    - 保养和维护 Protection and Maintenance

- 乙方负责质保期内的所有保修工作，包括但不限于：竣工验收合格移交前,由乙方负责施工成品保护、安全防护设施搭拆、文明清理等；

Before the completion acceptance and handover, the Party B shall be responsible for the protection of construction products, Safety protection facilities built and dismantled , housekeeping, etc.

- 竣工验收合格移交后，由乙方负责在质保期内的维护和修补；

After the completion acceptance and handover, the Party B shall be responsible for the maintenance and repair during the warranty period.

- 乙方采取区域分段移交场地的，在移交期间扔由乙方负责成品保护工作，整体移交后由乙方负责质保范围内的工作；

The Party B shall hand over the site in sections. During the handover, the Party B shall be responsible for the protection of construction products, and after the overall handover, the Party B shall be responsible for the work within the scope of warranty period.

- 成品保护工作一律以业主的要求和甲方的《成品保护管理细则》执行，相关费用已包含在合同综合单价中，材料由乙方负责；

The protection of finished products shall be carried out according to the requirements of the owner and the Finished Products Protection Management issued by the Party A. The relevant costs have been included in the comprehensive unit price of the contract, and the Party B shall be responsible for the materials.

  - 临时设施Temporary Facilities

- 乙方负责生产临建的施工及拆除（甲方只提供生产临建场地）；施工期间，乙方负责施工区域内现场临时施工道路的维护、场地清理、平整、并满足甲方的施工机械行驶要求；临时用水用电的材料提供、安装施工；生产临建的卫生清理、环境保护、消防等；施工区域内临时性设施的施工、围护、各类警示牌、宣传标语的张挂（各类警示牌、宣传标语由甲方提供）等，带有乙方公司LOGO的标语只允许出现在各自的施工区域，不允许出现在其他区域，除非经过甲方批准；生产临建的拆除和场地恢复需在竣工验收后7天内完成，具体包括不限于：吸烟点、休息区、加工棚、材料仓库、施工所需临时封堵等。

The Party B is responsible for construction and demolition of temporary facilities(the Party A only provides temporary construction site ); during the construction period, the Party B is responsible for the maintenance, site cleaning and leveling of temporary construction road in the construction area, and meet the driving requirements of the Party A's construction machinery; supply and installation of temporary water and electricity materials; temporary facilities of housekeeping ,environment protection,fire fighting and so on; the construction, enclosure of temporary facilities in the construction area, display of all kinds of warning signs and propaganda slogans (all kinds of warning signs and propaganda slogans shall be provided by the Party A), etc.; The slogan with theParty BLOGO is only allowed to appear in their respective construction areas, and is not appear in other areas, unless approved by the Party A. the demolition of temporary production buildings and site restoration shall be completed within 7 days after the completion acceptance, including but not limited to: smoking place , rest area, processing shed, material warehouse, temporary blocking required for construction, etc.

- 乙方临时设施应符合甲方定制化布置要求，且临时设施应包含劳工福利设施、应急防护设施等。现场应在现场设置定量的休息亭，每一个休息亭内需配备饮水点和吸烟点。

The temporary facilities of the Party B shall meet the customized layout requirements of the Party A, and the temporary facilities shall include labor welfare facilities, emergency protection facilities, etc. The site should be set up in the site of quantitative rest kiosks, each rest kiosk should be equipped with drinking water points and smoking points.

- 附件Attachment

Attachment 1 ：地形测量图GPSSurveys_DealsevilleSolar

Attachment 2：岩土勘察研究报告 Near Surface Geotechnical Investigation Report - Notsi PV -  Zone E

Attachment 3：水文调查报告 Notsi Hydro Report comments

Attachment 4：集中控制楼建筑图 ARCHITECTURAL PLANS & DETAILS FOR O&M BUILDING

Attachment 5：集中控制楼结构图 FOUNDATION & STRUCTURAL PLANS & DETAILS FOR O&M BUILDING

Attachment 6：门卫室建筑图 ARCHITECTURAL PLANS & DETAILS FOR GUARD HOUSE IN PV AREA

Attachment 7：门卫室结构图 FOUNDATION & STRUCTURAL PLANS & DETAILS FOR GUARD HOUSE IN PV AREA