## 建筑工程量清单报价表
建筑和安装工程量清单报价表 Bill of Quanty of Civil Works and Installation
金额单位：美元 Currency: USD
At present, there are no structural drawings. The list is only used for the construction bidding. The specific quantities of work will be reviewed and adjusted after the construction drawings are finalized.
编号 No. | 项目名称及规范 Item Name | 技术规格/项目特征 Description | 单位 Unit | 工程量 QTY | 单价 Unit Price (ZAR) | 合价 Total Price (ZAR) | 材料设备甲、乙供Materials supplied by | 备注
[5 empty] | 0 | 0
1 | 集中控制楼O&M Building | [6 empty] | 1 座/set
1） | 一般土建 Civil Works
| 土方开挖 Earthwork excavation | 1.Utilizing machine and manual assisstance; 2.Depth of Excavation refer to the drawing; 3.The soil should be placed closely , kept dry and be ready for backfilling purposes. 4.Other detail refer to Appendix-Technical Specification and drawing. | m³ | 3929.765 |  |  | 乙供 Party B
| 土方回填 Soil Backfilling | 1.The backfill soil is made from the soil obtained during the excavation of the foundation. 2.Each layer backfilling and the thickness is not more than 300mm; 3.Compacted to at least 95% of the maximum density based on the modified proctor test; 4.Other detail refer to Appendix-Technical Specification and drawing; | m³ | 3477.3655 |  |  | 乙供 Party B
| C20 垫层混凝土 Lean Concrete | 1. Pouring and curing concrete; 2. Shuttering and deshuttering; 3.Lay 2 layers of polyethylene vapor barrier; 4.Anti-termite measures below concrete; 5.Other detail refer to Appendix-Technical Specification and drawing; | m³ | 44.3282 |  |  | 乙供 Party B
| 钢筋混凝土基础 Reinforced Concrete Foundation | 1.Pouring and curing concrete; 2.Fabrication, installation and removal of formwork and support; 3.Reinforcement fabrication and installation; 4.Fabrication and installation of various embedded (sleeve and plate) parts; 5.Compressive stength of C30; 6.Other detail refer to Appendix-Technical Specification and drawing; | m³ | 151.232 |  |  | 乙供 Party B
| 砖墙基础Brick Foundation | 330厚砖砌体墙 330mm Mansory Brick Wall | m³ | 182.1281 |  |  | 乙供 Party B
| 集水罐基础(共2个)Base of the water tank(2) | 土方开挖 Earthwork excavation | m³ | 13.75 |  |  | 乙供 Party B
|  | 土方回填 Soil Backfilling | m³ | 8 |  |  | 乙供 Party B
|  | C20混凝土垫层 C20 concrete base layer | m³ | 0.64896 |  |  | 乙供 Party B
|  | 2.钢筋混凝土基础 Reinforced concrete foundation | m³ | 0.55873 |  |  | 乙供 Party B
|  | 3. 220厚砖砌体墙 220mm Mansory Brick Wall | m³ | 5.3073 |  |  | 乙供 Party B
|  | 4.150mm厚承台钢筋混凝土板 150mm Thick Slab of Reinforced Concrete C20 | m² | 0.79707 |  |  | 乙供 Party B
| 钢筋混凝土电缆沟Reinforced concrete cable trench | 1.Pouring and curing concrete; 2.Fabrication, installation and removal of formwork and support; 3.Reinforcement fabrication and installation; 4.Fabrication and installation of various embedded (sleeve and plate) parts; 5.Compressive stength of C30 6.type of cement is V(as per ASTM)+ Corrosion inhibitor; 7.other detail refer to Appendix-Technical Specification and drawing; | m³ | 2.9335 |  |  | 乙供 Party B
| 钢盖板 Steel slab | 1.Including the procurement, production and installation of materials 2other detail refer to Appendix-Technical Specification and drawing; | m² | 4.3549 |  |  | 乙供 Party B
| 钢筋混凝土基础梁 Reinforced Concrete Foundation Beam | 1.Pouring and curing concrete; 2.Fabrication, installation and removal of formwork and support; 3.Reinforcement fabrication and installation; 4.Fabrication and installation of various embedded (sleeve and plate) parts; 5.Compressive stength of C30 6.type of cement is V(as per ASTM)+ Corrosion inhibitor; 7.other detail refer to Appendix-Technical Specification and drawing; | m³ | 56.1851 |  |  | 乙供 Party B
| 钢筋混凝土基础柱 Reinforced Concrete Foundation Column | 1.Pouring and curing concrete; 2.Fabrication, installation and removal of formwork and support; 3.Reinforcement fabrication and installation; 4.Fabrication and installation of various embedded (sleeve and plate) parts; 5.Compressive stength of 28days cylindrical concrete is 38MPa; 6.type of cement is V(as per ASTM)+ Corrosion inhibitor; 7.other detail refer to Appendix-Technical Specification and drawing; | m³ | 15.5925 |  |  | 乙供 Party B
| 基础防水 Water-proof of Foundation | 1. Base cleaning; 2. Troweling (applying) paint, two layers of coal tar epoxy or polyurethane, total dry film thickness ≥600μm. 3.Other detail refer to Appendix-Technical Specification and drawing. | m² | 2150.63 |  |  | 乙供 Party B
| 普通地砖面层 Normal Ceramic Tile | 1) 6mm THICK CERAMIC TILE LAID IN CEMENT SAND MORTAR (1:5) 2) 75mm THICK P.C.C SCREED (1:4:8) 3) 50mm THICK BLINDING CONCRETE 4) 250–300 MICRON (μm) POLYTHENE MEMBRANE 5) G7 MATERIAL (MAX PARTICAL SIZE 37.5mm) UP 95% OF MDD AT OMC 6) COMPACTED PLATFORM | m² | 370.34 |  |  | 乙供 Party B
| 自流平环氧漆地面 Self-Levelling Epoxy | 1) GREY SELF-LEVELLING EPOXY 2) 100mm THICK POWER FLOATED CONCRETE SLAB 3) 100mm THICK SAND FILLING 4) G7 MATERIAL (MAX PARTICAL SIZE 37.5mm) UP 95% OF MDD AT OMC 5) COMPACTED PLATFORM | m² | 570.8828 |  |  | 乙供 Party B
| 钢筋混凝土结构框架 Reinforced concrete structural frame | 1. Pouring and curing concrete; 2. Fabrication, installation and removal of formwork and support; 3. Fabrication and installation of iron parts; 4.Compressive stength of C30; 5.Portland cement in accordance with ASTM C 150 type I with addition of pozzolan or type II; 6.Other parameters refer to the concrete specification ; 7.joint sealant(if require). | m³ | 107.0808 |  |  | 乙供 Party B
| 预制窗梁 Prefabricated window beam | 1.Details to check the construction drawings for specific details. | m³ | 3.4652 |  |  | 乙供 Party B
| 散水 Outdoor Drainage Floor | 1. 100mm Conocrete 20 Mpa； 2. 100mm Compacted Fill Material； 3. Compacted Platform / Earth | m² | 73.656 |  |  | 乙供 Party B
| 室外人行道 PAVING FOR SIDE WALK | 1.Material procurement, transportation and installation, Include kerb stone,Subgrade treatment, pavement construction 2.Details to check the construction drawings for specific details | m² | 355.025 |  |  | 乙供 Party B
| 台阶 Steps | 1.Details to check the construction drawings for specific details. | m² | 1.08 |  |  | 乙供 Party B
| 吊顶 Suspended Ceiling | 1. 4mm Thk Nutec Fibre/Gypsum Board/ Plastic Ceiling Supported On 38x50 WoodenBattens Attached/Suspended Bottom Of Truss @ 600mm c/c. | m² | 922.8782 |  |  | 乙供 Party B
| 踢脚线 Skirting | 6mm Thick Ceramic Tile Laid in Cement Sand Mortar (1:5) 100mm High Skirting | m | 428.16 |  |  | 乙供 Party B
| 金属屋檐排水沟 RAIN WATER GUTTER | 1. Fabrication and installation of eaves gutter; 2. Installation of downpipe; 3. Rainwater hopper; 4. Installation of siphon device; 5. Paint anti-corrosion; 6. Fabrication and installation of supports and hangers. 7.Other detail refer to Appendix-Technical Specification and drawing. | m | 97 |  |  | 乙供 Party B
| 屋面保温隔热 Thermal insulation of benzene panels for roof | 1.Extruded Polystyrene /knauf Insulation 150mm Thick | m² | 922.8782 |  |  | 乙供 Party B
| 屋面工程 Roofing project | Steel roof slab, wooden roof trusses and purlins,Purchase and installation . | m² | 1031.1129 |  |  | 乙供 Party B
| 40mm DPC | Under-floor waterproofing strip Purchase and installation . | m² | 180 |  |  | 乙供 Party B
| 220厚砖砌体外墙 220mm Mansory External Wall | 1.220mm THk. CMU wall; 2.Out side 220mm Face Brick Masonry,Inner Side Plaster Laid In 1:4 Csmortar Pained WithI Mulsion Paint; 3.3 hour fire rated; 4.Other detail refer to Appendix-Technical Specification and drawing; | m3 | 105.8023 |  |  | 乙供 Party B
| 200厚砖砌体内墙 200mm Mansory Internal Wall | 1.200mm THk. CMU wall; 2.Other detail refer to Appendix-Technical Specification and drawing; | m3 | 75.7708 |  |  | 乙供 Party B
| 外墙装饰（瓷砖） External Wall Finishing （Brick） | 1.Out side 220mm Face Brick Masonry | m² | 634.16 |  |  | 乙供 Party B
| 内墙装饰（瓷砖）Internal Wall Finishing (Paint) | 1.From FFL to 2100mm Height: 6mm thick porcelain tile on 20mmthk. Cement sand plaster (1:4) | m² | 104.16 |  |  | 乙供 Party B
| 内墙装饰（涂料）Internal Wall Finishing (Paint) | 1.Wall base cleaning; 2.Bottom treatment and troweling; 3.Coats of emulsion paint on 20mmthk. Cement sand plaster (1:4) 5.Other detail refer to Appendix-Technical Specification and drawing; | m² | 464.24 |  |  | 乙供 Party B
| 铝合金窗 Aluminum window | 1. Window (purchase), installation, assembly of hardware accessories, installation of ground spring, etc; 2.Other detail refer to Appendix-Technical Specification and drawing; | m² | 40.5 |  |  | 乙供 Party B
| 窗户防盗网Window Steel Grill and . | Steel grill refer to the drawing . | m² | 40.5 |  |  | 乙供 Party B
| 百叶窗帘 Venetian blind | aluminum alloy | m² | 40.5 |  |  | 乙供 Party B
| 铝合金门 Aluminum Door | 1. Door (purchase), installation, assembly of hardware accessories, installation of ground spring, etc; 2.Other detail refer to Appendix-Technical Specification and drawing. | m² | 9.24 |  |  | 乙供 Party B
| 金属门 Steel door | 1. Door (purchase), installation, assembly of hardware accessories, installation of ground spring, etc; 2.Other detail refer to Appendix-Technical Specification and drawing. | m² | 47.53 |  |  | 乙供 Party B
| 实木门 SOLID WOODEN | 1. Phenolic door (purchase), installation, assembly of hardware accessories, installation of ground spring, etc; 2.Other detail refer to Appendix-Technical Specification and drawing; | m² | 24.885 |  |  | 乙供 Party B
| 普通钢筋 Normal Rebars | 1.Reinforcement procurement、processing and installation; 2.Longtitudinal bar:D14~D25;Stirrup:D8~D12. | t | 10.7388 |  |  | 乙供 Party B
| 屋面检修爬梯 Roof maintenance ladder | Aluminum alloy material extension-type, 8m high |  | 1 |  |  | 乙供 Party B
| 标识牌 signboard |  | m² | 2 |  |  | 乙供 Party B
| 电缆竖井Cable shaft | 1mx1m made of iron sheet ,6m high | m | 6 |  |  | 乙供 Party B
| 电缆桥架 Cable Bridge | 1m width ,Suspension height 0.5m,made of iron sheet | m | 60 |  |  | 乙供 Party B
| 集水箱 Water tank(2个) | 2500 Litre Polyethylene Water Tank（2）,Including both the water supply pipe and the drainage pipe |  | 2 |  |  | 乙供 Party B
| 建筑给排水 Water supply and drainage | 1. Water supply pipe, drainage pipe, valve, flange, water meter, flowmeter, pressure gauge, faucet, shower nozzle, floor drain, cleaning hole, inspection hole, ventilation cap, sanitary ware, water pump adapter and other materials and installation; 2. Installation of water supply and drainage equipment; 3. Production and installation of pipe support and; 4 , Heat preservation paint, anti-corrosion protection, pipeline flushing, hydrostatic test; 5, Commissioning, etc; 6.Please provide product samples when the bidder makes the quotation.. | lot | urinal,2 sets; water closet,5 sets; floor drain,6 sets; washbasin,3 sets; shower,2 sets; 100Ø UPVC RAIN WATER PIPE,35m; Other auxiliary materials |  |  | 乙供 Party B
| 生活建筑通风空调 Ventilation and air conditioning | 1. Production and installation of air duct, air duct support, air vent, hood and air valve field equipment support; 2. Installation of ventilation and air conditioning equipment; 3. Heat preservation paint and anti-corrosion protection; 4. Commissioning; 5.Other detail refer to Appendix-Technical Specification and drawing. 6.Please provide product samples when the bidder makes the quotation.. | lot | 1)FCU/ACCU，wall mounted 3.5 KW, 10 sets 2)FCU/ACCU，wall mounted 5.3 KW, 3 sets 3)Axial Exhaust Fan 240L/s, 16 sets 4) Other auxiliary materials |  |  | 乙供 Party B
| 生活建筑照明 Lighting | 1.Lighting conduit and cable trough installation,; 2.Lighting conduit anti-corrosion,; 3.Hanger installation, 4.Cable laying, 5.Junction box installation, 6.lighting fixture installation, 7.Explosion-proof lamp installation, 8. Waterproof lamp installation, 9.Emergency lamp installation, 10.Lighting control panel installation and wiring, switch and socket installation, 11.Waterproof and explosion-proof switch installation, testing and commissioning 12. Please provide product samples when the bidder makes the quotation.. | lot | 1 1) 180 sets of lighting fixtures 2) Lighting low-voltage cable 5000 meters 3) DN20 pipe 2000 meters 4) 40 sets of sockets 5) 40 sets of switches 6) 3 distribution boxes inside the wall 7) Other auxiliary materials |  |  | 乙供 Party B
| 建筑接地 Earthing | 1. Lightning protection belt installation; 2. Lightning protection downlead installation; 3. Earthing device installation; 4.Other detail refer to Appendix-Technical Specification and drawing. | lot | 1 1) Grounding conductor/wire 500 meters 2) 20 grounding rods 3) 50 connectors 4) Other auxiliary materials |  |  | 乙供 Party B
3） | 电话和网络 O&M Building Telephone and LAN Network
| IP电话 Substation dispatch IP Phone |  | SET | 8 |  |  | 甲供 Party A
| PABX盘柜 PABX Panel (in O&M Building) | • PABX • 2 nos. Network Ethernet switch with PoE (Up to 26 ports) • 4 nos. Network Distribution Frame 24 ports Panel Sheet Steel Thickness = 2.5mm, IP Class: min. IP42, 2.4 m swing frame panel LxWxH=2400x800x800mm | SET | 1 |  |  | 甲供 Party A
| 电缆和电缆管 Cable and Conduit | as per detail design | LOT | 1 |  |  | 甲供 Party A
4） | UP系统 O&M Building UPS System
| AC UPS和电池 AC UPS System with Battery (8hr Backup) | Input Voltage : 0.230kV 1P 2W+G Output Voltage: 0.230kV 1P, 2W+G Inverter Output : 1kVA, 0.85-0.9 pf Incoming 20A , MCCB, 2P, 02 No's Outgoing , 10A, MCB, 2P, 06 No's The UPS system shall MANDATORILY consist of two (2) independently operating units. | SET | 1 |  |  | 甲供 Party A
5） | 监控 O&M Building CCTV System
| 室内监控 CCTV Camera (Indoor) | 5megapixels, INDOOR AUTODOME 360, IP CAMERA Effective Range 30mtrs | Nos | 7 |  |  | 甲供 Party A
| 室外监控 CCTV Camera (Outdoor) | 5megapixels, OUTDOOR FIXED BODY, IP CAMERA Effective Range 50mtrs | Nos | 5 |  |  | 甲供 Party A
| 交换机 24 Ports SFP, L2 Switch Manageable (in Plant Security & CCTV Server Panel) | Rack mounted L2 Manageable Switch (24port PoE Ethernet & 2 SFP Gigabit port) 10/100/1000 Mbps. | SET | 1 |  |  | 甲供 Party A
| OF配电箱 ODF Main distribution box (36 port) (in Plant Security & CCTV Server Panel) |  | SET | 1 |  |  | 甲供 Party A
| 电脑 Intel Core i7 desktop Computer (workstation in O&M control room) | Desktop Systems Core i7 (8th Gen), >=1.9GHz (8MB >= smart cache), 8GB RAM, 2TB HDD, & 2GB Graphic card, with all accessories (equivalent or higher). | SET | 1 |  |  | 甲供 Party A
| 监控屏幕 Monitoring LED 32” Screen (in O&M Building) | LED full HD 1920*1080P, 24”, 2 Ports of HDMI, analogue digital ports and with mounting stands (equivalent or higher). | SET | 1 |  |  | 甲供 Party A
| 光纤 Fiber Optic Cable | 4C Fiber Optic Cable (Single Mode, 9/125 µm, 1550 nm, ITU-T G.652, Coat in PE, 100% waterproof, adapted for buried) with splicing, pigtail, connectors PV area CCTV cable is exclusive from this part | METER | 400 |  |  | 甲供 Party A
| 网线 Cat 6 Cable Roll |  | METER | 500 |  |  | 甲供 Party A
6） | 消防系统 O&M Building Fire Detection and Alarm System (FDAS) | [5 empty] | 乙供 Party B
| 盘柜 Fire Alarm Repeater Panel (Addressable Type) | Fire Alarm Repeater Panel as per NFPA Standards | SET | 1 |  |  | 乙供 Party B
| 烟感探测器 Addressable Smoke Detector | Ceiling Mounted Addressable Photo-Electric Type Smoke Detectors with Base -Operating Voltage = 20~35VDC- As per BS 5839 | SET | 22 |  |  | 乙供 Party B
| Addressable multi-detector | Ceiling Mounted Addressable Photo-Electric Type Smoke Detectors with Base-Operating Voltage = 20~35VDC- As per BS 5839 | SET | 4 |  |  | 乙供 Party B
| 热感探测器 Addressable heat-detector | Ceiling Mounted Addressable Photo-Electric Type Smoke Detectors with Base -Operating Voltage = 20~35VDC - As per BS 5839 | SET | 1 |  |  | 乙供 Party B
| 紧急报警按钮 Manual Call Points with Break Glass Units | Manual Call Points with Break Glass Units: Conform to NFPA Standards, CE-CPR approved, Type A – simple action, Color of the mechanical enclosure: Red RAL 3000 MCP - conventional - 2 contacts, Equipped with 2 NO/NC contacts – 5 A – 24 VDC IP 30 - IK 07 | SET | 4 |  |  | 乙供 Party B
| 音响 Sounder with Strobe Lights | Fire Alarm Siren Strobe Lights: Red Color, Volume of up to 80 dB(A), Maximum current consumption of less than 4.05 mA, With Flash Light, IP66, 440 Hz up to 2,90 kHz Operating Voltage: 15 VDC to 33 VDC RAL 9010 | SET | 2 |  |  | 乙供 Party B
| 电缆 Fire Alarm Cable | 2C x 1.5 mm2 Cu/PVC/PVC 2 Hrs. Fire Rated Cables as per IEC-60331 | Meter | 700 |  |  | 乙供 Party B
| 电缆套管 Cable Conduits | 3/4" Conduit Stainless Steel Conduit | Meter | 700 |  |  | 乙供 Party B
7） | PPC盘柜装置 POWER PLANT CONTROLLER PANEL & EQUIPMENTS (PV PPC)
| SCADA服务器和PPC盘柜 PV Plant SCADA Server/PPC Panel | • 5 nos. SCADA Controllers • Main PV Server (19-inch rack) • Backup PV Server (19-inch rack) • Redundant network cards units • Redundant power supply • Main PV Ethernet Switch (Up to 28 ports) • Backup PV Ethernet Switch (Up to 28 ports) • PV PPC-1,2 (Master), PPC-3,4,5,6 (Slave-1), PPC-7,8,9,10 (Slave-2) • 2 nos. Fiber Optic Patch Tray • 2 nos. Firewalls • NTP Server • UPS with battery (8Hrs Backup) • KVM Switch Sheet Steel 2.5mm, IP Class: IP42, Exterior Color RAL 7032, Interior Color RAL 9010, 2.4 m swing frame panel | SET | 2 |  |  | 甲供 Party A
| 工程师站和LED屏幕 PV SCADA Engineering Workstation with 32" LED Screen | Tower Type, Power supply 90-250VDC/220VAC dual power supply Windows Server, PV software, Antivirus licensed, MODBUS License+IEC101/104+others as required communication ETHERNET LAN , IEC61850 compliant | SET | 2 |  |  | 甲供 Party A
8） | 低压电缆和通讯电缆 LV and Communication Cables | [5 empty] | 甲供 Party A
| AC Cables [For DC & UPS System] | 1mm2 | METER | 400 |  |  | 甲供 Party A
|  | 4C-16mm2 | METER | 1800 |  |  | 甲供 Party A
|  | 4C-4mm2 | METER | 4000 |  |  | 甲供 Party A
|  | 4C-95 mm2 | METER | 700 |  |  | 甲供 Party A
| Control Cables 0.6/1kV, CU/SWA/PVC, Fire-resistant (for 110VDC) | 4C-16 mm2 | METER | 700 |  |  | 甲供 Party A
|  | 4C-4 mm2 | METER | 600 |  |  | 甲供 Party A
| Communication Cables | CAT6 Ethernet Cable, FOC (SM), FOC (MM) , RS232/485. | LOT | 1 |  |  | 甲供 Party A
9） | 门禁系统 Access Control System for O&M Building
| 盘柜 Access Control Panel | • Server • Power Supply Module, DC24V, 3A | SET | 1 |  |  | 甲供 Party A
| 设备 Access Control equipment | • Card Reader • Keypads • Emergency Push Button • Electromagntic Lock • Door Contact | PCS | 8 |  |  | 甲供 Party A
| 门禁卡 ID Card |  | PCS | 15 |  |  | 甲供 Party A
| 制卡机 Card Maker |  | PCS | 1 |  |  | 甲供 Party A
| 电缆和套管 Cable and Conduit | as per detail design | LOT | 1 |  |  | 甲供 Party A
2 | 保安室Guard House
1） | 一般土建 Civil Works
| 土方开挖 Earthwork excavation | 1.Utilizing machine and manual assisstance; 2.Depth of Excavation refer to the drawing; 3.The soil should be placed closely , kept dry and be ready for backfilling purposes. 4.Other detail refer to Appendix-Technical Specification and drawing. | m³ | 41.925 |  |  | 乙供 Party B
| 土方回填 Soil Backfilling | 1.Backfill material transport is not more than 3.5Km; 2.Each layer backfilling and the thickness is not more than 300mm; 3.Compacted to at least 95% of the maximum density based on the modified proctor test; 4.Other detail refer to Appendix-Technical Specification and drawing; | m³ | 30.2986 |  |  | 乙供 Party B
| C20 垫层混凝土 Lean Concrete | 1. Pouring and curing concrete; 2. Shuttering and deshuttering; 3.Two layers of 150 micron polyethylene vapor barrier; 4.Anti-termite measures below concrete; 5.Other detail refer to Appendix-Technical Specification and drawing; | m³ | 1.5107 |  |  | 乙供 Party B
| 钢筋混凝土基础 Reinforced Concrete Foundation | 1.Pouring and curing concrete; 2.Fabrication, installation and removal of formwork and support; 3.Reinforcement fabrication and installation; 4.Fabrication and installation of various embedded (sleeve and plate) parts; 5.Compressive stength of C30; 6.Other detail refer to Appendix-Technical Specification and drawing; | m³ | 4.6998 |  |  | 乙供 Party B
| 砖墙基础Brick Foundation | 220厚砖砌体墙 330mm Mansory Brick Wall | m³ | 5.416 |  |  | 乙供 Party B
| 预制窗梁 Prefabricated window beam | 1.Details to check the construction drawings for specific details. | m³ | 0.345 |  |  | 乙供 Party B
| 普通地砖面层 Normal Ceramic Tile | 1) 6mm THICK CERAMIC TILE LAID IN CEMENT SAND MORTAR (1:5) 2) 75mm THICK P.C.C SCREED (1:4:8) 3) 50mm THICK BLINDING CONCRETE 4) 250–300 MICRON (μm) POLYTHENE MEMBRANE 5) G7 MATERIAL (MAX PARTICAL SIZE 37.5mm) UP 95% OF MDD AT OMC 6) COMPACTED PLATFORM | m² | 20.91 |  |  | 乙供 Party B
| 集水罐基础(共1个)Base of the water tank(1) | 土方开挖 Earthwork excavation | m³ | 2.4 |  |  | 乙供 Party B
|  | 土方回填 Soil Backfilling | m³ | 1.4259 |  |  | 乙供 Party B
|  | C20混凝土垫层 C20 concrete base layer | m³ | 0.29701 |  |  | 乙供 Party B
|  | 2.钢筋混凝土基础 Reinforced concrete foundation | m³ | 0.67712 |  |  | 乙供 Party B
|  | 3. 220厚砖砌体墙 220mm Mansory Brick Wall | m³ | 0.858 |  |  | 乙供 Party B
|  | 4.150mm厚钢筋混凝土板 150mm Thick Slab of Reinforced Concrete | m³ | 0.3465 |  |  | 乙供 Party B
| 集水箱 Water tank(1个) | 1000 Litre Polyethylene Water Tank（1）,Including both the water supply pipe and the drainage pipe |  | 1 |  |  | 乙供 Party B
| 室外人行道 PAVING FOR SIDE WALK | 1.Material procurement, transportation and installation, Include kerb stone,Subgrade treatment, pavement construction 2.Details to check the construction drawings for specific details | m² | 23 |  |  | 乙供 Party B
| 散水 Drainage Floor | 1. 100mm Conocrete 20 Mpa； 2. 100mm Compacted Fill Material； 3. Compacted Platform / Earth | m² | 11.04 |  |  | 乙供 Party B
| 吊顶 Suspended Ceiling | 1. 4mm Thk Nutec Fibre/Gypsum Board/ Plastic Ceiling Supported On 38x50 WoodenBattens Attached/Suspended Bottom Of Truss @ 600mm c/c. | m² | 20.91 |  |  | 乙供 Party B
| 踢脚线 Skirting | 6mm Thick Ceramic Tile Laid in Cement Sand Mortar (1:5) 100mm High Skirting | m | 18.4 |  |  | 乙供 Party B
| 屋面保温隔热 Thermal insulation of benzene panels for roof | 1.Extruded Polystyrene /knauf Insulation 150mm Thick | m² | 20.91 |  |  | 乙供 Party B
| 屋面工程 Roofing project | Steel roof slab, wooden roof trusses and purlins,Purchase and installation . | m² | 38.3284 |  |  | 乙供 Party B
| 40mm DPC | Under-floor waterproofing strip Purchase and installation . | m² | 7.5 |  |  | 乙供 Party B
| 220厚砖砌体外墙 220mm Mansory External Wall | 1.220mm THk. CMU wall; 2.Out side 220mm Face Brick Masonry,Inner Side Plaster Laid In 1:4 Csmortar Pained WithI Mulsion Paint; 3.3 hour fire rated; 4.Other detail refer to Appendix-Technical Specification and drawing; | m3 | 18.498 |  |  | 乙供 Party B
| 100厚砖砌体内墙 100mm Mansory Internal Wall | 1.200mm THk. CMU wall; 2.Other detail refer to Appendix-Technical Specification and drawing; | m3 | 1.316 |  |  | 乙供 Party B
| 外墙装饰（瓷砖） External Wall Finishing （ceramict） | 1.WALL EXTERIOR SIDE : FACE BRICK | m² | 59.685 |  |  | 乙供 Party B
| 内墙装饰（涂料）Internal Wall Finishing (Paint) | 1WALL INNER SIDE: 2 COATS OF EMULSION PAINT ON 20mmTHK. CEMENT SAND PLASTER (1:4) | m² | 74.928 |  |  | 乙供 Party B
| 内墙装饰（瓷砖）Internal Wall Finishing (ceramict) | FROM FFL TO 2100mm HEIGHT: 6mm THICK PORCELAIN TILE ON 20mmTHK. CEMENT SAND PLASTER (1:4) FROM 2100mm TO ROOF: 2 COATS OF EMULSION PAINT ON 20mm THK | m² | 15.792 |  |  | 乙供 Party B
| 铝合金窗 Metal window | 1. Window (purchase), installation, assembly of hardware accessories, installation of ground spring, etc; 2.Other detail refer to Appendix-Technical Specification and drawing; | m² | 6.84 |  |  | 乙供 Party B
| 金属门 Metal door | 1. Door (purchase), installation, assembly of hardware accessories, installation of ground spring, etc; 2.Other detail refer to Appendix-Technical Specification and drawing. | m² | 2.205 |  |  | 乙供 Party B
| 实木门 SOLID WOODEN FRAME | 1. Door (purchase), installation, assembly of hardware accessories, installation of ground spring, etc; 2.Other detail refer to Appendix-Technical Specification and drawing. | m² | 1.575 |  |  | 乙供 Party B
2） | 给排水、通风、照明 Water Supply And Drainage,Air Conditioning, Lighting | [5 empty] | 乙供 Party B
| 建筑给排水 Water supply and drainage | 1. Water supply pipe, drainage pipe, valve, flange, water meter, flowmeter, pressure gauge, faucet, shower nozzle, floor drain, cleaning hole, inspection hole, ventilation cap, sanitary ware, water pump adapter and other materials and installation; 2. Installation of water supply and drainage equipment; 3. Production and installation of pipe support and; 4 , Heat preservation paint, anti-corrosion protection, pipeline flushing, hydrostatic test; 5, Commissioning, etc; 6.Other detail refer to Appendix-Technical Specification and drawing. | lot | water closet,1 sets; floor drain,2 sets; washbasin,1 sets; shower,1 sets; 100Ø UPVC RAIN WATER PIPE,10m; Other auxiliary materials |  |  | 乙供 Party B
| 生活建筑通风空调 Ventilation and air conditioning | 1. Production and installation of air duct, air duct support, air vent, hood and air valve field equipment support; 2. Installation of ventilation and air conditioning equipment; 3. Heat preservation paint and anti-corrosion protection; 4. Commissioning; 5.Other detail refer to Appendix-Technical Specification and drawing. | lot | 1)FCU/ACCU，wall mounted 3.5 KW, 1 sets 2)Axial Exhaust Fan 240L/s, 1 sets 3) Other auxiliary materials |  |  | 乙供 Party B
| 生活建筑照明 Lighting | 1.Lighting conduit and cable trough installation,; 2.Lighting conduit anti-corrosion,; 3.Hanger installation, 4.Cable laying, 5.Junction box installation, 6.lighting fixture installation, 7.Explosion-proof lamp installation, 8. Waterproof lamp installation, 9.Emergency lamp installation, 10.Lighting control panel installation and wiring, switch and socket installation, 11.Waterproof and explosion-proof switch installation, testing and commissioning 12. Other detail refer to Appendix-Technical Specification and drawing. | lot | 1 1) 5 sets of lighting fixtures 2) Lighting low-voltage cable 500 meters 3) DN20 pipe 200 meters 4) 3 sets of sockets 5) 3 sets of switches 6) 1 distribution boxes inside the wall 7) Other auxiliary materials |  |  | 乙供 Party B
| 建筑接地 Earthing | 1. Lightning protection belt installation; 2. Lightning protection downlead installation; 3. Earthing device installation; 4.Other detail refer to Appendix-Technical Specification and drawing. | lot | 1 1) Grounding conductor 200 meters 2) 2 grounding rods 3) 8 connectors 4) Other auxiliary materials |  |  | 乙供 Party B
Total before VAT
VAT
Total after VAT
Note： 1. Steel structures installation includes rust removal and anticorrosive coating with brush; 2. Floor slab includes equipment miscellaneous foundation and support if any. 3. Slab includes secondary beams if any. 4. The unit price listed in the bill of quantities for this project is a comprehensive unit price, and the unit price has included all the work agreed in the contract, regardless of whether the relevant work is listed in the bill of quantities or not; 5. 100% of the amount will be paid if the RFI submitted is of APP status, 85% if the RFI submitted is of AWC status.